## INFO
Extension | DisplayName | Description | UnitType | DefaultValue | Applicable for Scenario Type | Required?
ENET | Electric Network | Models the characteristics and interactions of facilities and/or components of an electric network or market. Serves as a container for all objects in the electric network
Name | ModelName | Name of the network model. Permitted characters are letters, numbers, and underscore ("_"). The name should start with a letter, and have a length of 1 to 30 characters. |  |  |  | TRUE
BaseF | BaseFrequency | Base frequency for the entire network | FRQ | 50 [Hz] |  | FALSE
BaseS | BaseApparentPower | Nominal apparent power for conversion to network wide per unit system | SPOW | 100 [MVA] |  | FALSE
CRSType | CRS Type | Network coordinate reference system for the node locations |  | NONE |  | FALSE
Info | Info | Information related to the network model. Any character, including non-alphanumeric, is allowed |  |  |  | FALSE
ESUB | Electric Sub | Models a subset of nodes, branches, and externals of an electric network. An electric sub is branch-oriented, i.e., only electric branches can be assigned to an electric sub, and every electric branch belongs to only one electric sub
Name | Name | Object Name. Permitted characters are letters, numbers, and underscore ("_"). The name should start with a letter, and have a length of 1 to 30 characters. The name should be unique for each object type |  |  |  | TRUE
Info | Info | Information entered for the object. Any character, including non-alphanumeric, is allowed |  |  |  | FALSE
EGRP | Electric Group | Models a subset of different objects in an electric network. Except for the electric network, subs, and zones, any electric object can be added to an electric group. In contrast to electric subs and zones, electric groups do not follow any specific assignment rules. Thus, an electric object can be part of multiple electric groups
Name | Name | Object Name. Permitted characters are letters, numbers, and underscore ("_"). The name should start with a letter, and have a length of 1 to 30 characters. The name should be unique for each object type |  |  |  | TRUE
Info | Info | Information entered for the object. Any character, including non-alphanumeric, is allowed |  |  |  | FALSE
EZN | Electric Zone | Models a subset of nodes, branches, and externals of an electric network. An electric zone is node-oriented, i.e., only electric nodes can be assigned to an electric zone, and every electric node belongs to only one electric zone
Name | Name | Object Name. Permitted characters are letters, numbers, and underscore ("_"). The name should start with a letter, and have a length of 1 to 30 characters. The name should be unique for each object type |  |  |  | TRUE
Info | Info | Information entered for the object. Any character, including non-alphanumeric, is allowed |  |  |  | FALSE
ENO | Electric Node | Models a physical or virtual location in the electric network where electric power can be injected or extracted through externals (electric demand, generators, storages, etc.)
Name | Name | Object Name. Permitted characters are letters, numbers, and underscore ("_"). The name should start with a letter, and have a length of 1 to 30 characters. The name should be unique for each object type |  |  |  | TRUE
Alias | Alias | Alternative object name. Any character, including non-alphanumeric, is allowed |  |  |  | FALSE
BaseV | BaseVoltageMag | Nominal voltage magnitude | VOLT | 20 [kV] |  | FALSE
H | Elevation | Elevation | H | 0 [m] |  | FALSE
Info | Info | Information entered for the object. Any character, including non-alphanumeric, is allowed |  |  |  | FALSE
InService | InService | Indicates if an object is considered or disregarded in the execution of a scenario. Externals connected to the node inherit the "inService" status of the node |  | True |  | FALSE
Visible | Visible | If true, the object symbol will be visible in maps | NO | True |  | FALSE
VMAXDEF | DefMaxVoltageMag | Default maximum voltage magnitude in network per-unit | PU | 1.1 [pu] | SteadyACPF,SteadyACOPF,SteadyUACPF,QuasiDynamicACPF,QuasiDynamicACOPF,QuasiDynamicUACPF | FALSE
VMINDEF | DefMinVoltageMag | Default minimum voltage magnitude in network per-unit | PU | 0.9 [pu] | SteadyACPF,SteadyACOPF,SteadyUACPF,QuasiDynamicACPF,QuasiDynamicACOPF,QuasiDynamicUACPF | FALSE
X | X-Coordinate | Cartesian X or Longitude coordinate for visualizing the node in the map. Externals assigned to the node are not displayed | XY | 0 [km] |  | FALSE
Y | Y-Coordinate | Cartesian Y or Latitude coordinate for visualizing the node in the map. Externals assigned to the node are not displayed | XY | 0 [km] |  | FALSE
ZoneName | ZoneName | ZoneName of the zone the node belongs to |  | ZONE1 |  | FALSE
LI | Electric Line | Models the transport of electric power between two distant locations
Name | Name | Object Name. Permitted characters are letters, numbers, and underscore ("_"). The name should start with a letter, and have a length of 1 to 30 characters. The name should be unique for each object type |  |  |  | TRUE
FromName | FromNodeName | Name of FromNode |  |  |  | TRUE
ToName | ToNodeName | Name of ToNode |  |  |  | TRUE
Alias | Alias | Alternative object name. Any character, including non-alphanumeric, is allowed |  |  |  | FALSE
BB0DEF | DefZeroSeqSusceptance | Zero sequence line susceptance in line per unit system. The value is ignored for single-phase lines | PU | 0 [pu] | SteadyUACPF,QuasiDynamicUACPF | FALSE
BB0L | ZeroSeqSusceptancePerLength | Zero sequence line susceptance per unit length. The value is ignored for single-phase lines | GGL | 0 [μS/km] | SteadyUACPF,QuasiDynamicUACPF | FALSE
BBDEF | DefPositiveSeqSusceptance | Positive sequence shunt susceptance in branch per unit system. Used if "CalcImp" is false. Must be non-negative for electric line, because the shunt is capacitive | PU | 0 [pu] | SteadyACPF,SteadyACOPF,SteadyUACPF,QuasiDynamicACPF,QuasiDynamicACOPF,QuasiDynamicUACPF | FALSE
BBL | PositiveSeqSusceptancePerLength | Positive sequence line susceptance per unit length | GGL | 0 [μS/km] | SteadyACPF,SteadyACOPF,SteadyUACPF,QuasiDynamicACPF,QuasiDynamicACOPF,QuasiDynamicUACPF | FALSE
CalcImp | CalculateImpedances | Indicates how the network per unit impedances are calculated. If CalcImp is false, the branch per unit values are used for the calculation. If true, the per unit lenth properties of line are used |  | False | DCUCOPF,SteadyACPF,SteadyACOPF,SteadyUACPF,QuasiDynamicACPF,QuasiDynamicACOPF,QuasiDynamicUACPF | FALSE
DrawLine | DrawAsLine | If true, element will be drawn as a straight line and internal points will be neglected | NO | False |  | FALSE
IMAXDEF | DefMaxCurrent | Default maximum current magnitude in each phase of a balanced three-phase branch | CURR | ∞ [A] | SteadyACPF,SteadyACOPF,SteadyUACPF,QuasiDynamicACPF,QuasiDynamicACOPF,QuasiDynamicUACPF | FALSE
Info | Info | Information entered for the object. Any character, including non-alphanumeric, is allowed |  |  |  | FALSE
InService | InService | Indicates if an object is considered or disregarded in the execution of a scenario. Externals connected to the node inherit the "inService" status of the node |  | True |  | FALSE
L | LineLength | Total length of electric line | L | 10 [km] | DCUCOPF,SteadyACPF,SteadyACOPF,SteadyUACPF,QuasiDynamicACPF,QuasiDynamicACOPF,QuasiDynamicUACPF | FALSE
N | ImpedanceScalingFactor | Scaling factor for impedances. The series impedance will be divided by this value, and the shunt admittance will be multiplied by this value. Not used if "CalcImp" is false | ND | 1 | DCUCOPF,SteadyACPF,SteadyACOPF,SteadyUACPF,QuasiDynamicACPF,QuasiDynamicACOPF,QuasiDynamicUACPF | FALSE
PHASESINUSE | PhasesInUse | Identifies which phases of the line are connected, valid values are A, B, C, AB, AC, BC or ABC. |  | ABC | SteadyACPF,SteadyUACPF,QuasiDynamicACPF,QuasiDynamicUACPF | FALSE
PMAXDEF | DefMaxActivePower | Default maximum active power. It constrains the active power flow only in the positive flow direction, i.e. in the "FromNode" to "ToNode" flow direction, if a REVON event is defined for the electric network, otherwise both flow directions are constrained by PMAX. This property is the default value for the PMAX property if no PMAX event is defined in a scenario | PPOW | ∞ [MW] | DCUCOPF,SteadyACPF,SteadyACOPF,SteadyUACPF,QuasiDynamicACPF,QuasiDynamicACOPF,QuasiDynamicUACPF | FALSE
PMAXPRCDEF | DefMaxActivePowerPenPrice | Default penalty price for exceeding the maximum active power flow (PMAX). This property is the default value for the PMAXPRC property if no PMAXPRC event is defined in a scenario. Penalty is calculated as (P-PMAX) * PMAXPRC | NRGPRC | ∞ [$/MWh] | DCUCOPF | FALSE
PMAXREVDEF | DefMaxReverseActivePower | Default maximum active power in the negative flow direction. It constrains the active power flow only in the negative flow direction, i.e. in the "ToNode" to "FromNode" flow direction. This property is the default value for the PMAXREV property if no PMAXREV event is defined in a scenario. It is only considered if a REVON event is defined for the electric network | PPOW | ∞ [MW] | DCUCOPF | FALSE
PMAXREVPRCDEF | DefMaxReverseActivePowerPenPrice | Default penalty price for exceeding the maximum active power in negative flow direction (PMAXREV), i.e. "ToNode" to "FromNode" flow direction. This property is the default value for the PMAXREVPRC property if no PMAXREVPRC event is defined in a scenario. Penalty is calculated as (P-PMAXREV) * PMAXREVPRC | NRGPRC | ∞ [$/MWh] | DCUCOPF | FALSE
RATEDS | RatedApparentPower | Rated apparent power, assuming balanced three-phase object. If its value is NaN, which is the default, the network Base Apparent Power will be taken. It is used in the network per unit calculations. To change the value of a property to its default, right-click on the property and select “Set to the default value" | SPOW | NaN [MVA] | SteadyACPF,SteadyACOPF,SteadyUACPF,QuasiDynamicACPF,QuasiDynamicACOPF,QuasiDynamicUACPF | FALSE
RATEDV | RatedVoltage | Rated line-to-line voltage, assuming balanced three-phase object. If its value is NaN, which is the default, the network Base Voltage will be taken. It is used in the network per unit calculations. To change the value of a property to its default, right-click on the property and select “Set to the default value" | VOLT | NaN [kV] | SteadyACPF,SteadyACOPF,SteadyUACPF,QuasiDynamicACPF,QuasiDynamicACOPF,QuasiDynamicUACPF | FALSE
RR0DEF | DefZeroSeqResistance | Zero sequence line resistance in line per unit system. The value is ignored for single-phase lines | PU | 0 [pu] | SteadyUACPF,QuasiDynamicUACPF | FALSE
RR0L | ZeroSeqResistancePerLength | Zero sequence line resistance per unit length. The value is ignored for single-phase lines | RRL | 0 [Ω/km] | SteadyUACPF,QuasiDynamicUACPF | FALSE
RRDEF | DefPositiveSeqResistance | Positive sequence series resistance in branch per unit system. Defined to be non-negative. Used if "CalcImp" is false. | PU | 0 [pu] | DCUCOPF,SteadyACPF,SteadyACOPF,SteadyUACPF,QuasiDynamicACPF,QuasiDynamicACOPF,QuasiDynamicUACPF | FALSE
RRL | PositiveSeqResistancePerLength | Positive sequence line resistance per unit length | RRL | 0 [Ω/km] | DCUCOPF,SteadyACPF,SteadyACOPF,SteadyUACPF,QuasiDynamicACPF,QuasiDynamicACOPF,QuasiDynamicUACPF | FALSE
SMAXDEF | DefMaxApparentPower | Default maximum apparent power | SPOW | ∞ [MVA] | SteadyACPF,SteadyACOPF,SteadyUACPF,QuasiDynamicACPF,QuasiDynamicACOPF,QuasiDynamicUACPF | FALSE
SubName | SubName | Sub the branch belongs to |  |  |  | FALSE
Visible | Visible | If true, the object symbol will be visible in maps | NO | True |  | FALSE
XX0DEF | DefZeroSeqReactance | Zero sequence line reactance in line per unit system. Series capacitors can be modeled with negative values. The value is ignored for sigle-phase lines | PU | 0 [pu] | SteadyUACPF,QuasiDynamicUACPF | FALSE
XX0L | ZeroSeqReactancePerLength | Zero sequence line reactance per unit length. The value is ignored for single-phase lines | RRL | 0 [Ω/km] | SteadyUACPF,QuasiDynamicUACPF | FALSE
XXDEF | DefPositiveSeqReactance | Positive sequence series reactance in line per unit system. Series capacitor is represented by negative value. Used if "CalcImp" is false. | PU | 0 [pu] | DCUCOPF,SteadyACPF,SteadyACOPF,SteadyUACPF,QuasiDynamicACPF,QuasiDynamicACOPF,QuasiDynamicUACPF | FALSE
XXL | PositiveSeqReactancePerLength | Positive sequence line reactance per length | RRL | 0 [Ω/km] | DCUCOPF,SteadyACPF,SteadyACOPF,SteadyUACPF,QuasiDynamicACPF,QuasiDynamicACOPF,QuasiDynamicUACPF | FALSE
TRF | Electric Transformer | Models a local increase (step-up) or decrease (step-down) of voltage between areas of different voltage levels in the electric network
Name | Name | Object Name. Permitted characters are letters, numbers, and underscore ("_"). The name should start with a letter, and have a length of 1 to 30 characters. The name should be unique for each object type |  |  |  | TRUE
FromName | FromNodeName | Name of FromNode |  |  |  | TRUE
ToName | ToNodeName | Name of ToNode |  |  |  | TRUE
Alias | Alias | Alternative object name. Any character, including non-alphanumeric, is allowed |  |  |  | FALSE
BBDEF | DefPositiveSeqSusceptance | Positive sequence shunt susceptance in network per unit system. Used if "CalcImp" is false. Must be non-positive for electric transformer, because the shunt is inductive | PU | 0 [pu] | SteadyACPF,SteadyACOPF,SteadyUACPF,QuasiDynamicACPF,QuasiDynamicACOPF,QuasiDynamicUACPF | FALSE
CalcImp | CalculateImpedances | Indicates how the network per unit impedances are calculated. If CalcImp is false, the branch per unit values are used for the calculation. If true, the test-related properties of a transformer are used |  | False | DCUCOPF,SteadyACPF,SteadyACOPF,SteadyUACPF,QuasiDynamicACPF,QuasiDynamicACOPF,QuasiDynamicUACPF | FALSE
CTRLMODE | ControlMode | Control mode of the transformer, valid inputs are TapSet, Voltage, LineDropCompensation, or ReactivePower. Default is TapSet mode. Any TapSet event will override other control modes. |  | TapSet | SteadyACPF,SteadyUACPF,QuasiDynamicACPF,QuasiDynamicUACPF | FALSE
D | Deadband | Deadband, the full distance (ball) around the set point for which the tap keeps the vale from the previous time step. Value expressed in per unit at the base voltage of the the node under control for Voltage or LineDropCompensation control mode; or in per unit of the transformer rated apparent power for ReactivePower control mode | PU | 0 [pu] | SteadyACPF,SteadyUACPF,QuasiDynamicACPF,QuasiDynamicUACPF | FALSE
DrawLine | DrawAsLine | If true, element will be drawn as a straight line and internal points will be neglected | NO | False |  | FALSE
FROMRATEDV | FromRatedVoltage | Rated line-to-line voltage magnitude on the FromNode side, assuming balanced three-phase object. Used in transformer per unit system | VOLT | 200 [kV] | SteadyACPF,SteadyACOPF,SteadyUACPF,QuasiDynamicACPF,QuasiDynamicACOPF,QuasiDynamicUACPF | FALSE
GGDEF | DefPositiveSeqConductance | Positive sequence shunt conductance in branch per unit system. Used if "CalcImp" is false | PU | 0 [pu] | SteadyACPF,SteadyACOPF,SteadyUACPF,QuasiDynamicACPF,QuasiDynamicACOPF,QuasiDynamicUACPF | FALSE
IMAXDEF | DefMaxCurrent | Default maximum current magnitude in each phase of a balanced three-phase branch | CURR | ∞ [A] | SteadyACPF,SteadyACOPF,SteadyUACPF,QuasiDynamicACPF,QuasiDynamicACOPF,QuasiDynamicUACPF | FALSE
Info | Info | Information entered for the object. Any character, including non-alphanumeric, is allowed |  |  |  | FALSE
InService | InService | Indicates if an object is considered or disregarded in the execution of a scenario. Externals connected to the node inherit the "inService" status of the node |  | True |  | FALSE
IOL | OpenLoopLoss | Open loop (no‑load current), measured in the open‑circuit test and expressed as a percentage of the rated current of the transformer. Not used if "CalcImp" is false | PC | 0 [%] | SteadyACPF,SteadyACOPF,SteadyUACPF,QuasiDynamicACPF,QuasiDynamicACOPF,QuasiDynamicUACPF | FALSE
N | ImpedanceScalingFactor | Scaling factor for impedances. The series impedance will be divided by this value, and the shunt admittance will be multiplied by this value. Not used if "CalcImp" is false | ND | 1 | DCUCOPF,SteadyACPF,SteadyACOPF,SteadyUACPF,QuasiDynamicACPF,QuasiDynamicACOPF,QuasiDynamicUACPF | FALSE
PCU | CopperLoss | Copper (full load) loss, measured in the short circuit test in MW. Not applied if "CalcImp" is false | PPOW | 0.1 [MW] | SteadyACPF,SteadyACOPF,SteadyUACPF,QuasiDynamicACPF,QuasiDynamicACOPF,QuasiDynamicUACPF | FALSE
PFE | IronLoss | Iron (core) loss, measured in the open‑circuit test in MW. Not used if "CalcImp" is false | PPOW | 0 [MW] | SteadyACPF,SteadyACOPF,SteadyUACPF,QuasiDynamicACPF,QuasiDynamicACOPF,QuasiDynamicUACPF | FALSE
PHASESINUSE | PhasesInUse | Identifies which phases of the transformer are connected, valid values are A, B, C, or ABC. All of them are assumed to be connected to a neutral with zero impedance. |  | ABC | SteadyACPF,SteadyUACPF,QuasiDynamicACPF,QuasiDynamicUACPF | FALSE
PHISETDEF | DefPhaseShiftAngleSetPoint | Default value for phase shift angle | ANGLE | 0 [°] | SteadyACPF,SteadyACOPF,SteadyUACPF,QuasiDynamicACPF,QuasiDynamicACOPF,QuasiDynamicUACPF | FALSE
PMAXDEF | DefMaxActivePower | Default maximum active power. It constrains the active power flow only in the positive flow direction, i.e. in the "FromNode" to "ToNode" flow direction, if a REVON event is defined for the electric network, otherwise both flow directions are constrained by PMAX. This property is the default value for the PMAX property if no PMAX event is defined in a scenario | PPOW | ∞ [MW] | DCUCOPF,SteadyACPF,SteadyACOPF,SteadyUACPF,QuasiDynamicACPF,QuasiDynamicACOPF,QuasiDynamicUACPF | FALSE
PMAXPRCDEF | DefMaxActivePowerPenPrice | Default penalty price for exceeding the maximum active power flow (PMAX). This property is the default value for the PMAXPRC property if no PMAXPRC event is defined in a scenario. Penalty is calculated as (P-PMAX) * PMAXPRC | NRGPRC | ∞ [$/MWh] | DCUCOPF | FALSE
PMAXREVDEF | DefMaxReverseActivePower | Default maximum active power in the negative flow direction. It constrains the active power flow only in the negative flow direction, i.e. in the "ToNode" to "FromNode" flow direction. This property is the default value for the PMAXREV property if no PMAXREV event is defined in a scenario. It is only considered if a REVON event is defined for the electric network | PPOW | ∞ [MW] | DCUCOPF | FALSE
PMAXREVPRCDEF | DefMaxReverseActivePowerPenPrice | Default penalty price for exceeding the maximum active power in negative flow direction (PMAXREV), i.e. "ToNode" to "FromNode" flow direction. This property is the default value for the PMAXREVPRC property if no PMAXREVPRC event is defined in a scenario. Penalty is calculated as (P-PMAXREV) * PMAXREVPRC | NRGPRC | ∞ [$/MWh] | DCUCOPF | FALSE
QSETDEF | DefReactivePowerSetPoint | Reactive power set point in per unit of transformer base, applied only for ReactivePower control mode | PU | 1 [pu] | SteadyACPF,SteadyUACPF,QuasiDynamicACPF,QuasiDynamicUACPF | FALSE
RATEDS | RatedApparentPower | Rated apparent power, assuming balanced three-phase object. If its value is NaN, which is the default, the network Base Apparent Power will be taken. It is used in the network per unit calculations. To change the value of a property to its default, right-click on the property and select “Set to the default value" | SPOW | NaN [MVA] | SteadyACPF,SteadyACOPF,SteadyUACPF,QuasiDynamicACPF,QuasiDynamicACOPF,QuasiDynamicUACPF | FALSE
RDROP | LineDropResistance | Line drop resistance in per unit at the transformer base, applied only for the LineDropCompensation control mode | PU | 0 [pu] | SteadyACPF,SteadyUACPF,QuasiDynamicACPF,QuasiDynamicUACPF | FALSE
RemoteName | RemoteNodeName | Name of electric remote node whose voltage is controlled by this transformer |  |  | SteadyACPF,SteadyUACPF,QuasiDynamicACPF,QuasiDynamicUACPF | FALSE
RRDEF | DefPositiveSeqResistance | Positive sequence series resistance in branch per unit system. Defined to be non-negative. Used if "CalcImp" is false. | PU | 0 [pu] | DCUCOPF,SteadyACPF,SteadyACOPF,SteadyUACPF,QuasiDynamicACPF,QuasiDynamicACOPF,QuasiDynamicUACPF | FALSE
SMAXDEF | DefMaxApparentPower | Default maximum apparent power | SPOW | ∞ [MVA] | SteadyACPF,SteadyACOPF,SteadyUACPF,QuasiDynamicACPF,QuasiDynamicACOPF,QuasiDynamicUACPF | FALSE
SubName | SubName | Sub the branch belongs to |  |  |  | FALSE
TAPMAX | TapMax | Maximum value of available tap positions | ND | 2 | SteadyACPF,SteadyACOPF,SteadyUACPF,QuasiDynamicACPF,QuasiDynamicACOPF,QuasiDynamicUACPF | FALSE
TAPMIN | TapMin | Minimum value of available tap positions | ND | -2 | SteadyACPF,SteadyACOPF,SteadyUACPF,QuasiDynamicACPF,QuasiDynamicACOPF,QuasiDynamicUACPF | FALSE
TAPN | TapNeutral | Tap position where the off-nominal ratio (ONR) is 1 | ND | 0 | SteadyACPF,SteadyACOPF,SteadyUACPF,QuasiDynamicACPF,QuasiDynamicACOPF,QuasiDynamicUACPF | FALSE
TAPSETDEF | DefTapPositionSetPoint | Default value for tap position | ND | 0 | SteadyACPF,SteadyACOPF,SteadyUACPF,QuasiDynamicACPF,QuasiDynamicACOPF,QuasiDynamicUACPF | FALSE
TAPSide | TapSide | Indicates which side (FromNode or ToNode) of the transformer the tap is installed on. Valid inputs are "From" or "To" |  | From | SteadyACPF,SteadyACOPF,SteadyUACPF,QuasiDynamicACPF,QuasiDynamicACOPF,QuasiDynamicUACPF | FALSE
TAPSTEP | TapStepSize | Indicates how much off-nominal tap ratio changes [%] when tap position changes by one step | PC | 5 [%] | SteadyACPF,SteadyACOPF,SteadyUACPF,QuasiDynamicACPF,QuasiDynamicACOPF,QuasiDynamicUACPF | FALSE
TORATEDV | ToRatedVoltage | Rated line-to-line voltage magnitude on the ToNode side, assuming balanced three-phase object. Used in transformer per unit system | VOLT | 200 [kV] | SteadyACPF,SteadyACOPF,SteadyUACPF,QuasiDynamicACPF,QuasiDynamicACOPF,QuasiDynamicUACPF | FALSE
TRFModel | TrafoModel | Which equivalent circuit (T or PI) is used for branch admittance matrix |  | PI | SteadyACPF,SteadyACOPF,SteadyUACPF,QuasiDynamicACPF,QuasiDynamicACOPF,QuasiDynamicUACPF | FALSE
Visible | Visible | If true, the object symbol will be visible in maps | NO | True |  | FALSE
VMSETDEF | DefVoltageMagnitudeSetPoint | Default voltage magnitude set point in per unit of network base, applied only for Voltage and LineDropCompensation control modes | PU | 1 [pu] | SteadyACPF,SteadyUACPF,QuasiDynamicACPF,QuasiDynamicUACPF | FALSE
VSC | ShortCircuitVoltage | Short circuit voltage, measured in the short circuit test and expressed as a percentage of the rated voltage of the transformer. Not used if "CalcImp" is false | PC | 0.1 [%] | SteadyACPF,SteadyACOPF,SteadyUACPF,QuasiDynamicACPF,QuasiDynamicACOPF,QuasiDynamicUACPF | FALSE
XDROP | LineDropReactance | Line drop reactance in per unit at the transformer base, applied only for the LineDropCompensation control mode | PU | 0 [pu] | SteadyACPF,SteadyUACPF,QuasiDynamicACPF,QuasiDynamicUACPF | FALSE
XXDEF | DefPositiveSeqReactance | Positive sequence series reactance in branch per unit system. Used if "CalcImp" is false. | PU | 0 [pu] | DCUCOPF,SteadyACPF,SteadyACOPF,SteadyUACPF,QuasiDynamicACPF,QuasiDynamicACOPF,QuasiDynamicUACPF | FALSE
EDEM | Electric Demand | Models the extraction (consumption) of electric power at a node
Name | Name | Object Name. Permitted characters are letters, numbers, and underscore ("_"). The name should start with a letter, and have a length of 1 to 30 characters. The name should be unique for each object type |  |  |  | TRUE
NodeName | NodeName | Name of node the external is connected to |  |  |  | TRUE
Alias | Alias | Alternative object name. Any character, including non-alphanumeric, is allowed |  |  |  | FALSE
Info | Info | Information entered for the object. Any character, including non-alphanumeric, is allowed |  |  |  | FALSE
InService | InService | Indicates if an object is considered or disregarded in the execution of a scenario. Externals connected to the node inherit the "inService" status of the node |  | True |  | FALSE
LOADTYPE | LoadType | How the load is connected between phases and (or) neutral, valid values are Wye (balanced), Delta (balanced), A, B, C, AB, BC, or CA | NO | Wye | SteadyUACPF,QuasiDynamicUACPF | FALSE
PMAXDEF | DefMaxActivePower | Default maximum active power also used to calculate name plate capacity (NCAP). PMAX property is equal to PMAXDEF if no PMAX event is defined for a scenario | PPOW | ∞ [MW] | DCUCOPF,SteadyACPF,SteadyACOPF,SteadyUACPF,QuasiDynamicACPF,QuasiDynamicACOPF,QuasiDynamicUACPF | FALSE
PMAXPRCDEF | DefMaxActivePowerPenPrice | Default penalty price for exceeding the maximum active power (PMAX). The default event defined at the network level can be overwritten by a PMAXPRC event at the scenario level. Penalty is calculated as (P-PMAX) * PMAXPRCDEF | NRGPRC | ∞ [$/MWh] | DCUCOPF,SteadyACOPF,QuasiDynamicACOPF | FALSE
PMINDEF | DefMinActivePower | Default minimum active power. PMIN property is equal to PMINDEF if no PMIN event is defined for a scenario | PPOW | 0 [MW] | DCUCOPF,SteadyACPF,SteadyACOPF,SteadyUACPF,QuasiDynamicACPF,QuasiDynamicACOPF,QuasiDynamicUACPF | FALSE
PMINPRCDEF | DefMinActivePowerPenPrice | Default penalty price for exceeding the minimum active power (PMIN). The default event defined at the network level can be overwritten by a PMINPRC event at the scenario level. Penalty is calculated as (PMIN-P) * PMINPRCDEF | NRGPRC | ∞ [$/MWh] | DCUCOPF,SteadyACOPF,QuasiDynamicACOPF | FALSE
PSETDEF | DefActivePowerSetPoint | Default total active power set point. PSET is equal to PSETDEF if no PSET event is defined for a scenario | PPOW | 0 [MW] | DCUCOPF,SteadyACPF,SteadyACOPF,SteadyUACPF,QuasiDynamicACPF,QuasiDynamicACOPF,QuasiDynamicUACPF | FALSE
PSETPRCDEF | DefActivePowerSetpointPenPrice | Default penalty price for not meeting (curtailing) active power set point (PSETDEF). PSETPRC is equal to PSETPRCDEF if no PSETPRC event is defined for a scenario. Penalty is calculated as (PSET-P) * PSETPRC | NRGPRC | 2000 [$/MWh] | DCUCOPF,SteadyACOPF,QuasiDynamicACOPF | FALSE
PWF | PowerFactor | Power factor (apparent power magnitude divided by active power). Must be greater than 0 and no more than 1. If the reactive power is not set, will calculate a reactive power set-point based on this value, the power factor type and the active power set-point | ND | 1 | SteadyACPF,SteadyACOPF,SteadyUACPF,QuasiDynamicACPF,QuasiDynamicACOPF,QuasiDynamicUACPF | FALSE
PWFType | PowerFactorType | Power factor type. "ind" means lagging (inductive), while "cap" means leading (capacitive). The value does not matter for a unity (resistive) power factor. If the reactive power is not set, will calculate a reactive power set-point based on this value, the power factor and the active power set-point | NO | ind | SteadyACPF,SteadyACOPF,SteadyUACPF,QuasiDynamicACPF,QuasiDynamicACOPF,QuasiDynamicUACPF | FALSE
QMAXDEF | DefMaxReactivePower | Default maximum reactive power | QPOW | ∞ [MVAr] | SteadyACPF,SteadyACOPF,SteadyUACPF,QuasiDynamicACPF,QuasiDynamicACOPF,QuasiDynamicUACPF | FALSE
QMINDEF | DefMinReactivePower | Default minimum reactive power | QPOW | -∞ [MVAr] | SteadyACPF,SteadyACOPF,SteadyUACPF,QuasiDynamicACPF,QuasiDynamicACOPF,QuasiDynamicUACPF | FALSE
RATEDV | RatedVoltage | Rated line-to-line voltage, assuming balanced three-phase object. If its value is NaN, which is the default, the network Base Voltage will be taken. It is used in the network per unit calculations. To change the value of a property to its default, right-click on the property and select “Set to the default value" | VOLT | NaN [kV] | DCUCOPF,SteadyACPF,SteadyACOPF,SteadyUACPF,QuasiDynamicACPF,QuasiDynamicACOPF,QuasiDynamicUACPF | FALSE
Visible | Visible | If true, the object symbol will be visible in maps | NO | True |  | FALSE
EPS | Electric Prosumer | Base Object for Pumped Hydro Storage, External Grid and Generic Storage in the electric network
Name | Name | Object Name. Permitted characters are letters, numbers, and underscore ("_"). The name should start with a letter, and have a length of 1 to 30 characters. The name should be unique for each object type |  |  |  | TRUE
NodeName | NodeName | Name of node the external is connected to |  |  |  | TRUE
Alias | Alias | Alternative object name. Any character, including non-alphanumeric, is allowed |  |  |  | FALSE
Info | Info | Information entered for the object. Any character, including non-alphanumeric, is allowed |  |  |  | FALSE
InService | InService | Indicates if an object is considered or disregarded in the execution of a scenario. Externals connected to the node inherit the "inService" status of the node |  | True |  | FALSE
MaxDownRampDef | DefMaxDownRamp | Default maximum downward ramp rate for active power. It describes the rate at which the active power can decrease between two consecutive time steps. It defines the maximum rate of change (decrease) of the object between two consecutives timesteps. MaxDownRamp property is equal to MaxDownRampDef if no MaxDownRamp event is defined for a scenario | RAMP | ∞ [MW/min] | DCUCOPF | FALSE
MaxUpRampDef | DefMaxUpRamp | Default maximum upward ramp rate for active power. It describes the rate at which the active power can increase between two consecutive time steps. It defines the maximum rate of change (increase) of the object between two consecutives timesteps. MaxUpRamp property is equal to MaxUpRampDef if no MaxUpRamp event is defined for a scenario | RAMP | ∞ [MW/min] | DCUCOPF | FALSE
PDMAXDEF | DefMaxActivePowerDemand | Default maximum active power demand | PPOW | ∞ [MW] | DCUCOPF,SteadyACPF,SteadyACOPF,SteadyUACPF,QuasiDynamicACPF,QuasiDynamicACOPF,QuasiDynamicUACPF | FALSE
PDMAXPRCDEF | DefMaxActivePowerDemandPenPrice | DefMaxActivePowerDemandPenPrice | NRGPRC | ∞ [$/MWh] | SteadyACOPF,QuasiDynamicACOPF | FALSE
PDMINDEF | DefMinActivePowerDemand | DefMinActivePowerDemand | PPOW | 0 [MW] | DCUCOPF,SteadyACPF,SteadyACOPF,SteadyUACPF,QuasiDynamicACPF,QuasiDynamicACOPF,QuasiDynamicUACPF | FALSE
PDMINPRCDEF | DefMinActivePowerDemandPenPrice | DefMinActivePowerDemandPenPrice | NRGPRC | ∞ [$/MWh] | SteadyACOPF,QuasiDynamicACOPF | FALSE
PFSETDEF | DefActivePowerCompensationFactor | Default active power slack participation factor set point (does not apply in DCUCOPF). If participation factors are not provided (=0), slack will be distributed according to generator size | ND | 0 | SteadyACPF,SteadyUACPF,QuasiDynamicACPF,QuasiDynamicUACPF | FALSE
PGMAXDEF | DefMaxActivePowerGeneration | DefMaxActivePowerGeneration | PPOW | ∞ [MW] | DCUCOPF,SteadyACPF,SteadyACOPF,SteadyUACPF,QuasiDynamicACPF,QuasiDynamicACOPF,QuasiDynamicUACPF | FALSE
PGMAXPRCDEF | DefMaxActivePowerGenerationPenPrice | DefMaxActivePowerGenerationPenPrice | NRGPRC | ∞ [$/MWh] | SteadyACOPF,QuasiDynamicACOPF | FALSE
PGMINDEF | DefMinActivePowerGeneration | DefMinActivePowerGeneration | PPOW | 0 [MW] | DCUCOPF,SteadyACPF,SteadyACOPF,SteadyUACPF,QuasiDynamicACPF,QuasiDynamicACOPF,QuasiDynamicUACPF | FALSE
PGMINPRCDEF | DefMinActivePowerGenerationPenPrice | DefMinActivePowerGenerationPenPrice | NRGPRC | ∞ [$/MWh] | SteadyACOPF,QuasiDynamicACOPF | FALSE
PSETDEF | DefActivePowerSetPoint | Default total active power set point. PSET is equal to PSETDEF if no PSET event is defined for a scenario | PPOW | 0 [MW] | SteadyACPF,SteadyUACPF,QuasiDynamicACPF,QuasiDynamicUACPF | FALSE
PSETPRCDEF | DefActivePowerSetpointPenPrice | Default penalty price for not meeting (curtailing) active power set point (PSETDEF). PSETPRC is equal to PSETPRCDEF if no PSETPRC event is defined for a scenario. Penalty is calculated as (PSET-P) * PSETPRC | NRGPRC | 2000 [$/MWh] | DCUCOPF,SteadyACOPF,QuasiDynamicACOPF | FALSE
QMAXDEF | DefMaxReactivePower | Default maximum reactive power | QPOW | ∞ [MVAr] | SteadyACPF,SteadyACOPF,SteadyUACPF,QuasiDynamicACPF,QuasiDynamicACOPF,QuasiDynamicUACPF | FALSE
QMINDEF | DefMinReactivePower | Default minimum reactive power | QPOW | -∞ [MVAr] | SteadyACPF,SteadyACOPF,SteadyUACPF,QuasiDynamicACPF,QuasiDynamicACOPF,QuasiDynamicUACPF | FALSE
Visible | Visible | If true, the object symbol will be visible in maps | NO | True |  | FALSE
VMSETDEF | DefVoltageMagSetPoint | Default voltage magnitude set point | PU | 1 [pu] | SteadyACPF,SteadyACOPF,SteadyUACPF,QuasiDynamicACPF,QuasiDynamicACOPF,QuasiDynamicUACPF | FALSE
VOMDPriceDef | DefVOMDPrice | Default variable operational and maintenance cost per stored/charged energy | NRGPRC | 0 [$/MWh] | DCUCOPF,SteadyACOPF,QuasiDynamicACOPF | FALSE
VOMGPriceDef | DefVOMGPrice | Default variable operational and maintenance cost per generated/discharged energy | NRGPRC | 0 [$/MWh] | DCUCOPF,SteadyACOPF,QuasiDynamicACOPF | FALSE
ESTR | Electric Storage | Models the storage of electric energy in electric storage systems, such as battery, flywheel, or compressed air
Name | Name | Object Name. Permitted characters are letters, numbers, and underscore ("_"). The name should start with a letter, and have a length of 1 to 30 characters. The name should be unique for each object type |  |  |  | TRUE
NodeName | NodeName | Name of node the external is connected to |  |  |  | TRUE
Alias | Alias | Alternative object name. Any character, including non-alphanumeric, is allowed |  |  |  | FALSE
GENPHASES | GeneratorPhases | Identifies if the generator is three-phase or single-phase, if it is a single-phase, then to which phase it is connected, valid values are A, B, C, or ABC | NO | ABC | SteadyUACPF,QuasiDynamicUACPF | FALSE
Info | Info | Information entered for the object. Any character, including non-alphanumeric, is allowed |  |  |  | FALSE
InService | InService | Indicates if an object is considered or disregarded in the execution of a scenario. Externals connected to the node inherit the "inService" status of the node |  | True |  | FALSE
MaxCapDef | DefMaxStorageCapacity | Default Maximum storage capacity | NRG | ∞ [MJ] | DCUCOPF,SteadyACPF,SteadyACOPF,SteadyUACPF,QuasiDynamicACPF,QuasiDynamicACOPF,QuasiDynamicUACPF | FALSE
MaxDownRampDef | DefMaxDownRamp | Default maximum downward ramp rate for active power. It describes the rate at which the active power can decrease between two consecutive time steps. It defines the maximum rate of change (decrease) of the object between two consecutives timesteps. MaxDownRamp property is equal to MaxDownRampDef if no MaxDownRamp event is defined for a scenario | RAMP | ∞ [MW/min] | DCUCOPF | FALSE
MaxUpRampDef | DefMaxUpRamp | Default maximum upward ramp rate for active power. It describes the rate at which the active power can increase between two consecutive time steps. It defines the maximum rate of change (increase) of the object between two consecutives timesteps. MaxUpRamp property is equal to MaxUpRampDef if no MaxUpRamp event is defined for a scenario | RAMP | ∞ [MW/min] | DCUCOPF | FALSE
MinDownTimeDDDef | DefMinDownTimeDD | Default minimum down time between consecutive charging operations | TIME | 0 [h] | DCUCOPF | FALSE
MinDownTimeDGDef | DefMinDownTimeDG | Default minimum down time between consecutive charging-discharging operations | TIME | 0 [h] | DCUCOPF | FALSE
MinDownTimeGDDef | DefMinDownTimeGD | Default minimum down time between consecutive discharging-charging operations | TIME | 0 [h] | DCUCOPF | FALSE
MinDownTimeGGDef | DefMinDownTimeGG | Default minimum down time between consecutive discharging operations | TIME | 0 [h] | DCUCOPF | FALSE
MinUpTimeDDef | DefMinUpTimeD | Default minimum up time for charging operation | TIME | 0 [h] | DCUCOPF | FALSE
MinUpTimeGDef | DefMinUpTimeG | Default minimum up time for discharging operation | TIME | 0 [h] | DCUCOPF | FALSE
PDeff | ChargeEfficiency | Efficiency of charging process | ND | 1 | DCUCOPF,SteadyACPF,SteadyACOPF,SteadyUACPF,QuasiDynamicACPF,QuasiDynamicACOPF,QuasiDynamicUACPF | FALSE
PDMAXDEF | DefMaxChargePower | Default maximum charge rate for storage | PPOW | ∞ [MW] | DCUCOPF,SteadyACPF,SteadyACOPF,SteadyUACPF,QuasiDynamicACPF,QuasiDynamicACOPF,QuasiDynamicUACPF | FALSE
PDMAXPRCDEF | DefMaxChargePowerPenPrice | Default penalty price for maximum charge rate for storage | NRGPRC | ∞ [$/MWh] | SteadyACOPF,QuasiDynamicACOPF | FALSE
PDMINDEF | DefMinChargePower | Default minimum charge rate for storage | PPOW | 0 [MW] | DCUCOPF,SteadyACPF,SteadyACOPF,SteadyUACPF,QuasiDynamicACPF,QuasiDynamicACOPF,QuasiDynamicUACPF | FALSE
PDMINPRCDEF | DefMinChargePowerPenPrice | Default penalty price for min charge rate for storage | NRGPRC | ∞ [$/MWh] | SteadyACOPF,QuasiDynamicACOPF | FALSE
PFSETDEF | DefActivePowerCompensationFactor | Default active power slack participation factor set point (does not apply in DCUCOPF). If participation factors are not provided (=0), slack will be distributed according to generator size | ND | 0 | SteadyACPF,SteadyUACPF,QuasiDynamicACPF,QuasiDynamicUACPF | FALSE
PGeff | DischargeEfficiency | Efficiency of discharging process | ND | 1 | DCUCOPF,SteadyACPF,SteadyACOPF,SteadyUACPF,QuasiDynamicACPF,QuasiDynamicACOPF,QuasiDynamicUACPF | FALSE
PGMAXDEF | DefMaxDischargePower | Default maximum discharge rate | PPOW | ∞ [MW] | DCUCOPF,SteadyACPF,SteadyACOPF,SteadyUACPF,QuasiDynamicACPF,QuasiDynamicACOPF,QuasiDynamicUACPF | FALSE
PGMAXPRCDEF | DefMaxDischargePowerPenPrice | Default penalty price for maximum discharge rate | NRGPRC | ∞ [$/MWh] | SteadyACOPF,QuasiDynamicACOPF | FALSE
PGMINDEF | DefMinDischargePower | Default minimum discharge rate | PPOW | 0 [MW] | DCUCOPF,SteadyACPF,SteadyACOPF,SteadyUACPF,QuasiDynamicACPF,QuasiDynamicACOPF,QuasiDynamicUACPF | FALSE
PGMINPRCDEF | DefMinDischargePowerPenPrice | Default penalty price for minimum discharge rate | NRGPRC | ∞ [$/MWh] | SteadyACOPF,QuasiDynamicACOPF | FALSE
PSETDEF | DefActivePowerSetPoint | Default total active power set point. PSET is equal to PSETDEF if no PSET event is defined for a scenario | PPOW | 0 [MW] | SteadyACPF,SteadyUACPF,QuasiDynamicACPF,QuasiDynamicUACPF | FALSE
PSETPRCDEF | DefActivePowerSetpointPenPrice | Default penalty price for not meeting (curtailing) active power set point (PSETDEF). PSETPRC is equal to PSETPRCDEF if no PSETPRC event is defined for a scenario. Penalty is calculated as (PSET-P) * PSETPRC | NRGPRC | 2000 [$/MWh] | DCUCOPF,SteadyACOPF,QuasiDynamicACOPF | FALSE
QMAXDEF | DefMaxReactivePower | Default maximum reactive power | QPOW | ∞ [MVAr] | SteadyACPF,SteadyACOPF,SteadyUACPF,QuasiDynamicACPF,QuasiDynamicACOPF,QuasiDynamicUACPF | FALSE
QMINDEF | DefMinReactivePower | Default minimum reactive power | QPOW | -∞ [MVAr] | SteadyACPF,SteadyACOPF,SteadyUACPF,QuasiDynamicACPF,QuasiDynamicACOPF,QuasiDynamicUACPF | FALSE
QSETDEF | DefReactivePowerSetPoint | Default total reactive power set point | QPOW | 0 [MVAr] | SteadyACPF,SteadyACOPF,SteadyUACPF,QuasiDynamicACPF,QuasiDynamicACOPF,QuasiDynamicUACPF | FALSE
SOCMAXPRCDEF | DefStateOfChargeMaxPenPrice | Default penalty price for violating state of charge maximum constraint | NRGPRC | 1000000 [$/MWh] | DCUCOPF | FALSE
SOCMINPRCDEF | DefStateOfChargeMinPenPrice | Default penalty price for violating state of charge minimum constraint | NRGPRC | 1000000 [$/MWh] | DCUCOPF | FALSE
SOCSETPRCDEF | DefStateOfChargeSetPointPenPrice | Default penalty price for violating state of charge set point | NRGPRC | 1000000 [$/MWh] | DCUCOPF | FALSE
Visible | Visible | If true, the object symbol will be visible in maps | NO | True |  | FALSE
VOMDPriceDef | DefVOMDPrice | Default variable operational and maintenance cost per stored/charged energy | NRGPRC | 0 [$/MWh] | DCUCOPF,SteadyACOPF,QuasiDynamicACOPF | FALSE
VOMGPriceDef | DefVOMGPrice | Default variable operational and maintenance cost per generated/discharged energy | NRGPRC | 0 [$/MWh] | DCUCOPF,SteadyACOPF,QuasiDynamicACOPF | FALSE
SHT | Electric Shunt | Models a shunt reactor or capacitor. Shunt reactors are placed locally to control the over-voltages at electric nodes under light load conditions (consume reactive power to reduce the nodal voltage), while shunt capacitors are used to boost the voltage in a stressed system (supply reactive power to increase the nodal voltage)
Name | Name | Object Name. Permitted characters are letters, numbers, and underscore ("_"). The name should start with a letter, and have a length of 1 to 30 characters. The name should be unique for each object type |  |  |  | TRUE
NodeName | NodeName | Name of node the external is connected to |  |  |  | TRUE
Alias | Alias | Alternative object name. Any character, including non-alphanumeric, is allowed |  |  |  | FALSE
BSETDEF | DefShuntSusceptanceSetPoint | Injected reactive power at the rated voltage. Used to calculate the shunt susceptance. A positive value means the shunt is capacitive, otherwise it is inductive | QPOW | 0 [MVAr] | SteadyACPF,SteadyACOPF,SteadyUACPF,QuasiDynamicACPF,QuasiDynamicACOPF,QuasiDynamicUACPF | FALSE
GSETDEF | DefShuntConductanceSetPoint | Dissipated active power at the rated voltage. Used to calculate the shunt conductance | PPOW | 0 [MW] | SteadyACPF,SteadyACOPF,SteadyUACPF,QuasiDynamicACPF,QuasiDynamicACOPF,QuasiDynamicUACPF | FALSE
Info | Info | Information entered for the object. Any character, including non-alphanumeric, is allowed |  |  |  | FALSE
InService | InService | Indicates if an object is considered or disregarded in the execution of a scenario. Externals connected to the node inherit the "inService" status of the node |  | True |  | FALSE
RATEDV | RatedVoltage | Rated line-to-line voltage, assuming balanced three-phase object. If its value is NaN, which is the default, the network Base Voltage will be taken. It is used in the network per unit calculations. To change the value of a property to its default, right-click on the property and select “Set to the default value" | VOLT | NaN [kV] | DCUCOPF,SteadyACPF,SteadyACOPF,SteadyUACPF,QuasiDynamicACPF,QuasiDynamicACOPF,QuasiDynamicUACPF | FALSE
SHTTYPE | ShuntType | How the shunt is connected between phases and (or) neutral, valid values are Wye (balanced), Delta (balanced), A, B, C, AB, BC, or CA | NO | Wye | SteadyUACPF,QuasiDynamicUACPF | FALSE
Visible | Visible | If true, the object symbol will be visible in maps | NO | True |  | FALSE
WIND | Wind Generator | Models the injection of electric power from a wind generator. The electric power generation profile for a wind generator can be generated from wind weather resource data and the characteristics of the wind generator (wind turbine power curve, hub height, etc.)
Name | Name | Object Name. Permitted characters are letters, numbers, and underscore ("_"). The name should start with a letter, and have a length of 1 to 30 characters. The name should be unique for each object type |  |  |  | TRUE
NodeName | NodeName | Name of node the external is connected to |  |  |  | TRUE
Alias | Alias | Alternative object name. Any character, including non-alphanumeric, is allowed |  |  |  | FALSE
C0DEF | DefConstCostCoeff | Default constant coefficient of operational cost | C | 0 [$] | SteadyACOPF,QuasiDynamicACOPF | FALSE
C1DEF | DefLinCostCoeff | Default linear coefficient of operational cost | NRGPRC | 0 [$/MWh] | SteadyACOPF,QuasiDynamicACOPF | FALSE
C2DEF | DefQuadCostCoeff | Default quadratic coefficient of operational cost | NRG2PRC | 0 [$/MWh²] | SteadyACOPF,QuasiDynamicACOPF | FALSE
CALCDFLT | CalcDefault | Calculate default values for maximum ramp rate (MaxUpRampDef and MaxDownRampDef), and (when applicable) startup time (MinUpTimeDef and MinDownTimeDef), generator capability curve (GCC), heat rate curve (HR0, HR1, and HR2) |  | SELECT | DCUCOPF,SteadyACPF,SteadyACOPF,SteadyUACPF,QuasiDynamicACPF,QuasiDynamicACOPF,QuasiDynamicUACPF | FALSE
HubHeight | HubHeight | Hub height of the wind generator used for calculating the wind speed. Considered only when the generation profile is derived from the weather resource data retrieved from a data provider | H | 100 [m] |  | FALSE
Info | Info | Information entered for the object. Any character, including non-alphanumeric, is allowed |  |  |  | FALSE
InService | InService | Indicates if an object is considered or disregarded in the execution of a scenario. Externals connected to the node inherit the "inService" status of the node |  | True |  | FALSE
Lat | Latitude | Latitude of the object based on WGS84 Datum. Used only to retrieve weather resource data from external data providers for PV and WIND objects | LATLONG | 0 |  | FALSE
Long | Longitude | Longitude of the object based on WGS84 Datum. Used only to retrieve weather resource data from external data providers for PV and WIND objects | LATLONG | 0 |  | FALSE
LOSSES | TotalSystemLosses | Total system losses. Considered only when the generation profile is derived from the weather resource data retrieved from a data provider | PC | 14.08 [%] |  | FALSE
MaxDownRampDef | DefMaxDownRamp | Default maximum downward ramp rate for active power. It describes the rate at which the active power can decrease between two consecutive time steps. It defines the maximum rate of change (decrease) of the object between two consecutives timesteps. MaxDownRamp property is equal to MaxDownRampDef if no MaxDownRamp event is defined for a scenario | RAMP | ∞ [MW/min] | DCUCOPF | FALSE
MaxUpRampDef | DefMaxUpRamp | Default maximum upward ramp rate for active power. It describes the rate at which the active power can increase between two consecutive time steps. It defines the maximum rate of change (increase) of the object between two consecutives timesteps. MaxUpRamp property is equal to MaxUpRampDef if no MaxUpRamp event is defined for a scenario | RAMP | ∞ [MW/min] | DCUCOPF | FALSE
PFSETDEF | DefActivePowerCompensationFactor | Default active power slack participation factor set point (does not apply in DCUCOPF). If participation factors are not provided (=0), slack will be distributed according to generator size | ND | 0 | SteadyACPF,SteadyUACPF,QuasiDynamicACPF,QuasiDynamicUACPF | FALSE
PMAXDEF | DefMaxActivePower | Default maximum active power also used to calculate name plate capacity (NCAP). PMAX property is equal to PMAXDEF if no PMAX event is defined for a scenario | PPOW | ∞ [MW] | DCUCOPF,SteadyACPF,SteadyACOPF,SteadyUACPF,QuasiDynamicACPF,QuasiDynamicACOPF,QuasiDynamicUACPF | FALSE
PMAXPRCDEF | DefMaxActivePowerPenPrice | Default penalty price for exceeding the maximum active power (PMAX). The default event defined at the network level can be overwritten by a PMAXPRC event at the scenario level. Penalty is calculated as (P-PMAX) * PMAXPRCDEF | NRGPRC | ∞ [$/MWh] | DCUCOPF,SteadyACOPF,QuasiDynamicACOPF | FALSE
PMINDEF | DefMinActivePower | Default minimum active power. PMIN property is equal to PMINDEF if no PMIN event is defined for a scenario | PPOW | 0 [MW] | DCUCOPF,SteadyACPF,SteadyACOPF,SteadyUACPF,QuasiDynamicACPF,QuasiDynamicACOPF,QuasiDynamicUACPF | FALSE
PMINPRCDEF | DefMinActivePowerPenPrice | Default penalty price for exceeding the minimum active power (PMIN). The default event defined at the network level can be overwritten by a PMINPRC event at the scenario level. Penalty is calculated as (PMIN-P) * PMINPRCDEF | NRGPRC | ∞ [$/MWh] | DCUCOPF,SteadyACOPF,QuasiDynamicACOPF | FALSE
PSETDEF | DefActivePowerSetPoint | Default total active power set point. PSET is equal to PSETDEF if no PSET event is defined for a scenario | PPOW | 0 [MW] | DCUCOPF,SteadyACPF,SteadyACOPF,SteadyUACPF,QuasiDynamicACPF,QuasiDynamicACOPF,QuasiDynamicUACPF | FALSE
PSETPRCDEF | DefActivePowerSetpointPenPrice | Default penalty price for not meeting (curtailing) active power set point (PSETDEF). PSETPRC is equal to PSETPRCDEF if no PSETPRC event is defined for a scenario. Penalty is calculated as (PSET-P) * PSETPRC | NRGPRC | 2000 [$/MWh] | DCUCOPF,SteadyACOPF,QuasiDynamicACOPF | FALSE
QMAXDEF | DefMaxReactivePower | Default maximum reactive power | QPOW | ∞ [MVAr] | SteadyACPF,SteadyACOPF,SteadyUACPF,QuasiDynamicACPF,QuasiDynamicACOPF,QuasiDynamicUACPF | FALSE
QMINDEF | DefMinReactivePower | Default minimum reactive power | QPOW | -∞ [MVAr] | SteadyACPF,SteadyACOPF,SteadyUACPF,QuasiDynamicACPF,QuasiDynamicACOPF,QuasiDynamicUACPF | FALSE
QSETDEF | DefReactivePowerSetPoint | Default total reactive power set point | QPOW | 0 [MVAr] | SteadyACPF,SteadyACOPF,SteadyUACPF,QuasiDynamicACPF,QuasiDynamicACOPF,QuasiDynamicUACPF | FALSE
RATEDS | RatedApparentPower | Rated apparent power, assuming balanced three-phase object. If its value is NaN, which is the default, the network Base Apparent Power will be taken. It is used in the network per unit calculations. To change the value of a property to its default, right-click on the property and select “Set to the default value" | SPOW | NaN [MVA] | SteadyUACPF,QuasiDynamicUACPF | FALSE
RATEDV | RatedVoltage | Rated line-to-line voltage, assuming balanced three-phase object. If its value is NaN, which is the default, the network Base Voltage will be taken. It is used in the network per unit calculations. To change the value of a property to its default, right-click on the property and select “Set to the default value" | VOLT | NaN [kV] | DCUCOPF,SteadyACPF,SteadyACOPF,SteadyUACPF,QuasiDynamicACPF,QuasiDynamicACOPF,QuasiDynamicUACPF | FALSE
RRN | PerUnitNeutralResistance | Neutral resistance in pu in the generator base system | PU | 0 [pu] | SteadyUACPF,QuasiDynamicUACPF | FALSE
RRSE | PerUnitOutputResistance | Per phase output resistance in pu in the generator base system | PU | 0 [pu] | SteadyUACPF,QuasiDynamicUACPF | FALSE
Visible | Visible | If true, the object symbol will be visible in maps | NO | True |  | FALSE
VOMPriceDef | DefVOMPrice | Default variable operational and maintenance price per produced energy. VOMPrice property is equal to VOMPriceDef if no VOMPrice event is defined for a scenario | NRGPRC | 0 [$/MWh] | DCUCOPF,SteadyACOPF,QuasiDynamicACOPF | FALSE
WDFile | WeatherDataFile | Path to weather data file. A folder named "WeatherDataFile" is created after retrieving data from an external data provider |  |  |  | FALSE
WTPCName | WindTurbPowCurveName | Name of wind turbine power curve object. Considered only when the generation profile is derived from the weather resource data retrieved from a data provider. An exaustive list of wind tubine power curves is available in the user folder. |  |  |  | FALSE
XXN | PerUnitNeutralReactance | Neutral reactance in in pu in the generator base system | PU | 0 [pu] | SteadyUACPF,QuasiDynamicUACPF | FALSE
XXSE | PerUnitOutputReactance | Per phase output reactance in in pu in the generator base system | PU | 0 [pu] | SteadyUACPF,QuasiDynamicUACPF | FALSE
PV | Solar Generator | Models the injection of electric power from a solar generator. The electric power generation profile for a solar generator can be generated from solar weather resource data and the characteristics of the solar generator (PanelType, Tilt Angle, etc.)
Name | Name | Object Name. Permitted characters are letters, numbers, and underscore ("_"). The name should start with a letter, and have a length of 1 to 30 characters. The name should be unique for each object type |  |  |  | TRUE
NodeName | NodeName | Name of node the external is connected to |  |  |  | TRUE
Alias | Alias | Alternative object name. Any character, including non-alphanumeric, is allowed |  |  |  | FALSE
ArrayType | ArrayType | Tilt system of the array of the solar generator. It describes whether the PV modules are fixed, or they move to track the movement of the sun across the sky with one or two axes of rotation. Considered only when the generation profile is derived from the weather resource data retrieved from a data provider |  | Fixed |  | FALSE
Azimuth | AzimuthAngle | Azimuth angle of the solar generator, North = 0 [°], East = 90 [°], South = 180 [°], West = 270 [°]. For a fixed array, it is the angle clockwise from true north describing the direction that the array faces. For an array with one-axis tracking, it is the angle clockwise from true north of the axis of rotation. It does not apply to arrays with two-axis tracking. Considered only when the generation profile is derived from the weather resource data retrieved from a data provider | ANGLE | 180 [°] |  | FALSE
C0DEF | DefConstCostCoeff | Default constant coefficient of operational cost | C | 0 [$] | SteadyACOPF,QuasiDynamicACOPF | FALSE
C1DEF | DefLinCostCoeff | Default linear coefficient of operational cost | NRGPRC | 0 [$/MWh] | SteadyACOPF,QuasiDynamicACOPF | FALSE
C2DEF | DefQuadCostCoeff | Default quadratic coefficient of operational cost | NRG2PRC | 0 [$/MWh²] | SteadyACOPF,QuasiDynamicACOPF | FALSE
CALCDFLT | CalcDefault | Calculate default values for maximum ramp rate (MaxUpRampDef and MaxDownRampDef), and (when applicable) startup time (MinUpTimeDef and MinDownTimeDef), generator capability curve (GCC), heat rate curve (HR0, HR1, and HR2) |  | SELECT | DCUCOPF,SteadyACPF,SteadyACOPF,SteadyUACPF,QuasiDynamicACPF,QuasiDynamicACOPF,QuasiDynamicUACPF | FALSE
DCACRatio | DCACPowerRatio | DC-AC power ratio of the solar generator. It is the ratio of the array's DC rated size to the inverter's AC rated size. Considered only when the generation profile is derived from the weather resource data retrieved from a data provider | ND | 1.1 |  | FALSE
GENPHASES | GeneratorPhases | Identifies if the generator is three-phase or single-phase, if it is a single-phase, then to which phase it is connected, valid values are A, B, C, or ABC | NO | ABC | SteadyUACPF,QuasiDynamicUACPF | FALSE
IMAXPU | MaxCurrentMagPerUnit | Maximum current magnitude in per-unit based on the apparent power and voltage ratings | PU | 1.1 [pu] | SteadyUACPF,QuasiDynamicUACPF | FALSE
Info | Info | Information entered for the object. Any character, including non-alphanumeric, is allowed |  |  |  | FALSE
InService | InService | Indicates if an object is considered or disregarded in the execution of a scenario. Externals connected to the node inherit the "inService" status of the node |  | True |  | FALSE
InvEff | InverterEfficiency | Inverter efficiency of the solar generator. Defined as the inverter's rated AC power output divided by its rated DC power output. Considered only when the generation profile is derived from the weather resource data retrieved from a data provider | PC | 96 [%] |  | FALSE
Lat | Latitude | Latitude of the object based on WGS84 Datum. Used only to retrieve weather resource data from external data providers for PV and WIND objects | LATLONG | 0 |  | FALSE
Long | Longitude | Longitude of the object based on WGS84 Datum. Used only to retrieve weather resource data from external data providers for PV and WIND objects | LATLONG | 0 |  | FALSE
LOSSES | TotalSystemLosses | Total system losses. Considered only when the generation profile is derived from the weather resource data retrieved from a data provider | PC | 14.08 [%] |  | FALSE
MaxDownRampDef | DefMaxDownRamp | Default maximum downward ramp rate for active power. It describes the rate at which the active power can decrease between two consecutive time steps. It defines the maximum rate of change (decrease) of the object between two consecutives timesteps. MaxDownRamp property is equal to MaxDownRampDef if no MaxDownRamp event is defined for a scenario | RAMP | ∞ [MW/min] | DCUCOPF | FALSE
MaxUpRampDef | DefMaxUpRamp | Default maximum upward ramp rate for active power. It describes the rate at which the active power can increase between two consecutive time steps. It defines the maximum rate of change (increase) of the object between two consecutives timesteps. MaxUpRamp property is equal to MaxUpRampDef if no MaxUpRamp event is defined for a scenario | RAMP | ∞ [MW/min] | DCUCOPF | FALSE
ModuleType | ModuleType | Type of solar modules of the solar generator. Approximate nominal efficiencies are 19% for standard, 21% for premium, and 18% for thin film. Considered only when the generation profile is derived from the weather resource data retrieved from a data provider |  | Standard |  | FALSE
PFSETDEF | DefActivePowerCompensationFactor | Default active power slack participation factor set point (does not apply in DCUCOPF). If participation factors are not provided (=0), slack will be distributed according to generator size | ND | 0 | SteadyACPF,SteadyUACPF,QuasiDynamicACPF,QuasiDynamicUACPF | FALSE
PMAXDEF | DefMaxActivePower | Default maximum active power also used to calculate name plate capacity (NCAP). PMAX property is equal to PMAXDEF if no PMAX event is defined for a scenario | PPOW | ∞ [MW] | DCUCOPF,SteadyACPF,SteadyACOPF,SteadyUACPF,QuasiDynamicACPF,QuasiDynamicACOPF,QuasiDynamicUACPF | FALSE
PMAXPRCDEF | DefMaxActivePowerPenPrice | Default penalty price for exceeding the maximum active power (PMAX). The default event defined at the network level can be overwritten by a PMAXPRC event at the scenario level. Penalty is calculated as (P-PMAX) * PMAXPRCDEF | NRGPRC | ∞ [$/MWh] | DCUCOPF,SteadyACOPF,QuasiDynamicACOPF | FALSE
PMINDEF | DefMinActivePower | Default minimum active power. PMIN property is equal to PMINDEF if no PMIN event is defined for a scenario | PPOW | 0 [MW] | DCUCOPF,SteadyACPF,SteadyACOPF,SteadyUACPF,QuasiDynamicACPF,QuasiDynamicACOPF,QuasiDynamicUACPF | FALSE
PMINPRCDEF | DefMinActivePowerPenPrice | Default penalty price for exceeding the minimum active power (PMIN). The default event defined at the network level can be overwritten by a PMINPRC event at the scenario level. Penalty is calculated as (PMIN-P) * PMINPRCDEF | NRGPRC | ∞ [$/MWh] | DCUCOPF,SteadyACOPF,QuasiDynamicACOPF | FALSE
PSETDEF | DefActivePowerSetPoint | Default total active power set point. PSET is equal to PSETDEF if no PSET event is defined for a scenario | PPOW | 0 [MW] | DCUCOPF,SteadyACPF,SteadyACOPF,SteadyUACPF,QuasiDynamicACPF,QuasiDynamicACOPF,QuasiDynamicUACPF | FALSE
PSETPRCDEF | DefActivePowerSetpointPenPrice | Default penalty price for not meeting (curtailing) active power set point (PSETDEF). PSETPRC is equal to PSETPRCDEF if no PSETPRC event is defined for a scenario. Penalty is calculated as (PSET-P) * PSETPRC | NRGPRC | 2000 [$/MWh] | DCUCOPF,SteadyACOPF,QuasiDynamicACOPF | FALSE
QMAXDEF | DefMaxReactivePower | Default maximum reactive power | QPOW | ∞ [MVAr] | SteadyACPF,SteadyACOPF,SteadyUACPF,QuasiDynamicACPF,QuasiDynamicACOPF,QuasiDynamicUACPF | FALSE
QMINDEF | DefMinReactivePower | Default minimum reactive power | QPOW | -∞ [MVAr] | SteadyACPF,SteadyACOPF,SteadyUACPF,QuasiDynamicACPF,QuasiDynamicACOPF,QuasiDynamicUACPF | FALSE
QSETDEF | DefReactivePowerSetPoint | Default total reactive power set point | QPOW | 0 [MVAr] | SteadyACPF,SteadyACOPF,SteadyUACPF,QuasiDynamicACPF,QuasiDynamicACOPF,QuasiDynamicUACPF | FALSE
RATEDS | RatedApparentPower | Rated apparent power, assuming balanced three-phase object. If its value is NaN, which is the default, the network Base Apparent Power will be taken. It is used in the network per unit calculations. To change the value of a property to its default, right-click on the property and select “Set to the default value" | SPOW | NaN [MVA] | SteadyUACPF,QuasiDynamicUACPF | FALSE
RATEDV | RatedVoltage | Rated line-to-line voltage, assuming balanced three-phase object. If its value is NaN, which is the default, the network Base Voltage will be taken. It is used in the network per unit calculations. To change the value of a property to its default, right-click on the property and select “Set to the default value" | VOLT | NaN [kV] | DCUCOPF,SteadyACPF,SteadyACOPF,SteadyUACPF,QuasiDynamicACPF,QuasiDynamicACOPF,QuasiDynamicUACPF | FALSE
Tilt | TiltAngle | Tilt angle of the solar generator relative to horizon, 0 [°] is horizontal 90 [°] is vertical. For a fixed array, it is the angle from horizontal of the array where 0° = horizontal, and 90° = vertical. For arrays with one-axis tracking, it is the angle from horizontal of the tracking axis. The tilt angle does not apply to arrays with two-axis tracking. Considered only when the generation profile is derived from the weather resource data retrieved from a data provider | ANGLE | 0 [°] |  | FALSE
Visible | Visible | If true, the object symbol will be visible in maps | NO | True |  | FALSE
VMAXPU | MaxVoltageMagPerUnit | Maximum voltage magnitude in per-unit based on the rated voltage | PU | 1.1 [pu] | SteadyUACPF,QuasiDynamicUACPF | FALSE
VMINPU | MinVoltageMagPerUnit | Minimum voltage magnitude in per-unit based on the rated voltage | PU | 0.9 [pu] | SteadyUACPF,QuasiDynamicUACPF | FALSE
VOMPriceDef | DefVOMPrice | Default variable operational and maintenance price per produced energy. VOMPrice property is equal to VOMPriceDef if no VOMPrice event is defined for a scenario | NRGPRC | 0 [$/MWh] | DCUCOPF,SteadyACOPF,QuasiDynamicACOPF | FALSE
WDFile | WeatherDataFile | Path to weather data file. A folder named "WeatherDataFile" is created after retrieving data from an external data provider |  |  |  | FALSE
XGEN | Generic Generator | Models a generator or an external network injecting electric power into the electric network
Name | Name | Object Name. Permitted characters are letters, numbers, and underscore ("_"). The name should start with a letter, and have a length of 1 to 30 characters. The name should be unique for each object type |  |  |  | TRUE
NodeName | NodeName | Name of node the external is connected to |  |  |  | TRUE
Alias | Alias | Alternative object name. Any character, including non-alphanumeric, is allowed |  |  |  | FALSE
C0DEF | DefConstCostCoeff | Default constant coefficient of operational cost | C | 0 [$] | SteadyACOPF,QuasiDynamicACOPF | FALSE
C1DEF | DefLinCostCoeff | Default linear coefficient of operational cost | NRGPRC | 0 [$/MWh] | SteadyACOPF,QuasiDynamicACOPF | FALSE
C2DEF | DefQuadCostCoeff | Default quadratic coefficient of operational cost | NRG2PRC | 0 [$/MWh²] | SteadyACOPF,QuasiDynamicACOPF | FALSE
CALCDFLT | CalcDefault | Calculate default values for maximum ramp rate (MaxUpRampDef and MaxDownRampDef), and (when applicable) startup time (MinUpTimeDef and MinDownTimeDef), generator capability curve (GCC), heat rate curve (HR0, HR1, and HR2) |  | SELECT | DCUCOPF,SteadyACPF,SteadyACOPF,SteadyUACPF,QuasiDynamicACPF,QuasiDynamicACOPF,QuasiDynamicUACPF | FALSE
GenType | GeneratorType | Specifies the generator type | NO | NONE |  | FALSE
Info | Info | Information entered for the object. Any character, including non-alphanumeric, is allowed |  |  |  | FALSE
InService | InService | Indicates if an object is considered or disregarded in the execution of a scenario. Externals connected to the node inherit the "inService" status of the node |  | True |  | FALSE
MaxDownRampDef | DefMaxDownRamp | Default maximum downward ramp rate for active power. It describes the rate at which the active power can decrease between two consecutive time steps. It defines the maximum rate of change (decrease) of the object between two consecutives timesteps. MaxDownRamp property is equal to MaxDownRampDef if no MaxDownRamp event is defined for a scenario | RAMP | ∞ [MW/min] | DCUCOPF | FALSE
MaxUpRampDef | DefMaxUpRamp | Default maximum upward ramp rate for active power. It describes the rate at which the active power can increase between two consecutive time steps. It defines the maximum rate of change (increase) of the object between two consecutives timesteps. MaxUpRamp property is equal to MaxUpRampDef if no MaxUpRamp event is defined for a scenario | RAMP | ∞ [MW/min] | DCUCOPF | FALSE
PFSETDEF | DefActivePowerCompensationFactor | Default active power slack participation factor set point (does not apply in DCUCOPF). If participation factors are not provided (=0), slack will be distributed according to generator size | ND | 0 | SteadyACPF,SteadyUACPF,QuasiDynamicACPF,QuasiDynamicUACPF | FALSE
PMAXDEF | DefMaxActivePower | Default maximum active power also used to calculate name plate capacity (NCAP). PMAX property is equal to PMAXDEF if no PMAX event is defined for a scenario | PPOW | ∞ [MW] | DCUCOPF,SteadyACPF,SteadyACOPF,SteadyUACPF,QuasiDynamicACPF,QuasiDynamicACOPF,QuasiDynamicUACPF | FALSE
PMAXPRCDEF | DefMaxActivePowerPenPrice | Default penalty price for exceeding the maximum active power (PMAX). The default event defined at the network level can be overwritten by a PMAXPRC event at the scenario level. Penalty is calculated as (P-PMAX) * PMAXPRCDEF | NRGPRC | ∞ [$/MWh] | DCUCOPF,SteadyACOPF,QuasiDynamicACOPF | FALSE
PMINDEF | DefMinActivePower | Default minimum active power. PMIN property is equal to PMINDEF if no PMIN event is defined for a scenario | PPOW | 0 [MW] | DCUCOPF,SteadyACPF,SteadyACOPF,SteadyUACPF,QuasiDynamicACPF,QuasiDynamicACOPF,QuasiDynamicUACPF | FALSE
PMINPRCDEF | DefMinActivePowerPenPrice | Default penalty price for exceeding the minimum active power (PMIN). The default event defined at the network level can be overwritten by a PMINPRC event at the scenario level. Penalty is calculated as (PMIN-P) * PMINPRCDEF | NRGPRC | ∞ [$/MWh] | DCUCOPF,SteadyACOPF,QuasiDynamicACOPF | FALSE
PSETDEF | DefActivePowerSetPoint | Default total active power set point. PSET is equal to PSETDEF if no PSET event is defined for a scenario | PPOW | 0 [MW] | SteadyACPF,SteadyUACPF,QuasiDynamicACPF,QuasiDynamicUACPF | FALSE
PSETPRCDEF | DefActivePowerSetpointPenPrice | Default penalty price for not meeting (curtailing) active power set point (PSETDEF). PSETPRC is equal to PSETPRCDEF if no PSETPRC event is defined for a scenario. Penalty is calculated as (PSET-P) * PSETPRC | NRGPRC | 2000 [$/MWh] | DCUCOPF,SteadyACOPF,QuasiDynamicACOPF | FALSE
QMAXDEF | DefMaxReactivePower | Default maximum reactive power | QPOW | ∞ [MVAr] | SteadyACPF,SteadyACOPF,SteadyUACPF,QuasiDynamicACPF,QuasiDynamicACOPF,QuasiDynamicUACPF | FALSE
QMINDEF | DefMinReactivePower | Default minimum reactive power | QPOW | -∞ [MVAr] | SteadyACPF,SteadyACOPF,SteadyUACPF,QuasiDynamicACPF,QuasiDynamicACOPF,QuasiDynamicUACPF | FALSE
RATEDS | RatedApparentPower | Rated apparent power, assuming balanced three-phase object. If its value is NaN, which is the default, the network Base Apparent Power will be taken. It is used in the network per unit calculations. To change the value of a property to its default, right-click on the property and select “Set to the default value" | SPOW | NaN [MVA] | SteadyUACPF,QuasiDynamicUACPF | FALSE
RATEDV | RatedVoltage | Rated line-to-line voltage, assuming balanced three-phase object. If its value is NaN, which is the default, the network Base Voltage will be taken. It is used in the network per unit calculations. To change the value of a property to its default, right-click on the property and select “Set to the default value" | VOLT | NaN [kV] | DCUCOPF,SteadyACPF,SteadyACOPF,SteadyUACPF,QuasiDynamicACPF,QuasiDynamicACOPF,QuasiDynamicUACPF | FALSE
RRN | PerUnitNeutralResistance | Neutral resistance in pu in the generator base system | PU | 0 [pu] | SteadyUACPF,QuasiDynamicUACPF | FALSE
RRSE | PerUnitOutputResistance | Per phase output resistance in pu in the generator base system | PU | 0 [pu] | SteadyUACPF,QuasiDynamicUACPF | FALSE
Visible | Visible | If true, the object symbol will be visible in maps | NO | True |  | FALSE
VMSETDEF | DefVoltageMagSetPoint | Default voltage magnitude set point | PU | 1 [pu] | SteadyACPF,SteadyACOPF,SteadyUACPF,QuasiDynamicACPF,QuasiDynamicACOPF,QuasiDynamicUACPF | FALSE
VOMPriceDef | DefVOMPrice | Default variable operational and maintenance price per produced energy. VOMPrice property is equal to VOMPriceDef if no VOMPrice event is defined for a scenario | NRGPRC | 0 [$/MWh] | DCUCOPF,SteadyACOPF,QuasiDynamicACOPF | FALSE
XXN | PerUnitNeutralReactance | Neutral reactance in in pu in the generator base system | PU | 0 [pu] | SteadyUACPF,QuasiDynamicUACPF | FALSE
XXSE | PerUnitOutputReactance | Per phase output reactance in in pu in the generator base system | PU | 0 [pu] | SteadyUACPF,QuasiDynamicUACPF | FALSE
HYDP | Hydro Plant | Models a hydro power plant consisting of one or more hydro generators. Water flows into the hydro power plant either from inflow (rain, etc.), water turbinated by another hydro power plant, or spillage from a hydro power plant. Hydro power plants have a maximum and minimum reservoir volume; the difference determines the volume that can be turbinated through a hydro generator. The hydro power plant has three outflow types, namely, outflow, turbination, and spilling
Name | Name | Object Name. Permitted characters are letters, numbers, and underscore ("_"). The name should start with a letter, and have a length of 1 to 30 characters. The name should be unique for each object type |  |  |  | TRUE
Alias | Alias | Alternative object name. Any character, including non-alphanumeric, is allowed |  |  |  | FALSE
BYPASSMAXDEF | DefMaxBypassFlow | Default maximum total flow bypassing turbines through hydro plant | HQVOL | ∞ [m³/s] | DCUCOPF | FALSE
BYPASSMAXPRCDEF | DefMaxBypassFlowPenPrice | Default maximum total flow bypassing turbine through hydro plant penalty price | VOLPRC | ∞ [$/m³] | DCUCOPF | FALSE
INFLOWDEF | DefInflow | Default inflow to hydro power plant | HQVOL | 0 [m³/s] | DCUCOPF | FALSE
Info | Info | Information entered for the object. Any character, including non-alphanumeric, is allowed |  |  |  | FALSE
InService | InService | Indicates if an object is considered or disregarded in the execution of a scenario. Externals connected to the node inherit the "inService" status of the node |  | True |  | FALSE
OUTFLOWDEF | DefOutflow | Default flow rate leaving the hydro power plant for irrigation and other purposes | HQVOL | 0 [m³/s] | DCUCOPF | FALSE
PUMPMAXDEF | DefMaxPumpFlow | Default maximum total pumped flow through hydro plant | HQVOL | ∞ [m³/s] | DCUCOPF | FALSE
PUMPMAXPRCDEF | DefMaxPumpFlowPenPrice | Default maximum total pumped flow through hydro plant penalty price | VOLPRC | ∞ [$/m³] | DCUCOPF | FALSE
SPILLMAXDEF | DefMaxSpillFlow | Default maximum total spilled flow through hydro power plant | HQVOL | ∞ [m³/s] | DCUCOPF | FALSE
SPILLMAXPRCDEF | DefMaxSpillFlowPenPrice | Default maximum total spilled flow through hydro power plant penalty price | VOLPRC | ∞ [$/m³] | DCUCOPF | FALSE
SPILLMINDEF | DefMinSpillFlow | Default minimum total spilled flow through hydro power plant | HQVOL | 0 [m³/s] | DCUCOPF | FALSE
SPILLMINPRCDEF | DefMinSpillFlowPenPrice | Default minimum total spilled flow through hydro power plant penalty price | VOLPRC | 0 [$/m³] | DCUCOPF | FALSE
SPILLPRCDEF | DefSpillPenPrice | Default penalty price for spilled flow | VOLPRC | 0.01 [$/m³] | DCUCOPF | FALSE
SpillToName | SpillToName | Name of hydro power plant receiving spilled water flow |  |  | DCUCOPF | FALSE
TURBMAXDEF | DefMaxTurbFlow | Default maximum total turbinated flow through hydro power plant | HQVOL | ∞ [m³/s] | DCUCOPF | FALSE
TURBMAXPRCDEF | DefMaxTurbFlowPenPrice | Default maximum total turbinated flow through hydro power plant penalty price | VOLPRC | ∞ [$/m³] | DCUCOPF | FALSE
TURBMINDEF | DefMinTurbFlow | Default minimum total turbinated flow through hydro power plant | HQVOL | 0 [m³/s] | DCUCOPF | FALSE
TurbToName | TurbToName | Name of hydro power plant receiving turbinated water flow |  |  | DCUCOPF | FALSE
VOLMAXDEF | DefMaxResVolume | Default maximum reservoir volume | VOL | ∞ [m³] | DCUCOPF | FALSE
VOLMAXPRCDEF | DefMaxResVolumePenPrice | Default maximum reservoir volume penalty price | VOLPRC | 1000000 [$/m³] | DCUCOPF | FALSE
VOLMINDEF | DefMinResVolume | Default minimum reservoir volume | VOL | 0 [m³] | DCUCOPF | FALSE
VOLMINPRCDEF | DefMinResVolumePenPrice | Default minimum reservoir volume penalty price | VOLPRC | 1000000 [$/m³] | DCUCOPF | FALSE
VOLSETPRCDEF | DefResVolumeSetPointPenPrice | Default penalty price for curtailing reservoir volume set point | VOLPRC | 1000000 [$/m³] | DCUCOPF | FALSE
HGEN | Hydro Generator | Models the injection of electric power from a hydro generator. The amount of electricity produced depends on the volumetric flow rate (TURB) driving the hydro turbines and a coefficient describing the active power generation per volumetric rate (PCOEFF). A hydro generator is always connected to a hydro power plant
Name | Name | Object Name. Permitted characters are letters, numbers, and underscore ("_"). The name should start with a letter, and have a length of 1 to 30 characters. The name should be unique for each object type |  |  |  | TRUE
NodeName | NodeName | Name of node the external is connected to |  |  |  | TRUE
PlantName | HydroPlantName | Name of the hydro power plant the generator belongs to | NO |  |  | TRUE
Alias | Alias | Alternative object name. Any character, including non-alphanumeric, is allowed |  |  |  | FALSE
C0DEF | DefConstCostCoeff | Default constant coefficient of operational cost | C | 0 [$] | SteadyACOPF,QuasiDynamicACOPF | FALSE
C1DEF | DefLinCostCoeff | Default linear coefficient of operational cost | NRGPRC | 0 [$/MWh] | SteadyACOPF,QuasiDynamicACOPF | FALSE
C2DEF | DefQuadCostCoeff | Default quadratic coefficient of operational cost | NRG2PRC | 0 [$/MWh²] | SteadyACOPF,QuasiDynamicACOPF | FALSE
CALCDFLT | CalcDefault | Calculate default values for maximum ramp rate (MaxUpRampDef and MaxDownRampDef), and (when applicable) startup time (MinUpTimeDef and MinDownTimeDef), generator capability curve (GCC), heat rate curve (HR0, HR1, and HR2) |  | SELECT | DCUCOPF,SteadyACPF,SteadyACOPF,SteadyUACPF,QuasiDynamicACPF,QuasiDynamicACOPF,QuasiDynamicUACPF | FALSE
Info | Info | Information entered for the object. Any character, including non-alphanumeric, is allowed |  |  |  | FALSE
InService | InService | Indicates if an object is considered or disregarded in the execution of a scenario. Externals connected to the node inherit the "inService" status of the node |  | True |  | FALSE
MaxDownRampDef | DefMaxDownRamp | Default maximum downward ramp rate for active power. It describes the rate at which the active power can decrease between two consecutive time steps. It defines the maximum rate of change (decrease) of the object between two consecutives timesteps. MaxDownRamp property is equal to MaxDownRampDef if no MaxDownRamp event is defined for a scenario | RAMP | ∞ [MW/min] | DCUCOPF | FALSE
MaxUpRampDef | DefMaxUpRamp | Default maximum upward ramp rate for active power. It describes the rate at which the active power can increase between two consecutive time steps. It defines the maximum rate of change (increase) of the object between two consecutives timesteps. MaxUpRamp property is equal to MaxUpRampDef if no MaxUpRamp event is defined for a scenario | RAMP | ∞ [MW/min] | DCUCOPF | FALSE
PCOEFF | FlowToPowerGenerationCoeff | Active power generation per volumetric flow rate driving hydro turbine | POWQVOL | 0 [MW/m³/s] | DCUCOPF | FALSE
PFSETDEF | DefActivePowerCompensationFactor | Default active power slack participation factor set point (does not apply in DCUCOPF). If participation factors are not provided (=0), slack will be distributed according to generator size | ND | 0 | SteadyACPF,SteadyUACPF,QuasiDynamicACPF,QuasiDynamicUACPF | FALSE
PMAXDEF | DefMaxActivePower | Default maximum active power also used to calculate name plate capacity (NCAP). PMAX property is equal to PMAXDEF if no PMAX event is defined for a scenario | PPOW | ∞ [MW] | DCUCOPF,SteadyACPF,SteadyACOPF,SteadyUACPF,QuasiDynamicACPF,QuasiDynamicACOPF,QuasiDynamicUACPF | FALSE
PMAXPRCDEF | DefMaxActivePowerPenPrice | Default penalty price for exceeding the maximum active power (PMAX). The default event defined at the network level can be overwritten by a PMAXPRC event at the scenario level. Penalty is calculated as (P-PMAX) * PMAXPRCDEF | NRGPRC | ∞ [$/MWh] | DCUCOPF,SteadyACOPF,QuasiDynamicACOPF | FALSE
PMINDEF | DefMinActivePower | Default minimum active power. PMIN property is equal to PMINDEF if no PMIN event is defined for a scenario | PPOW | 0 [MW] | DCUCOPF,SteadyACPF,SteadyACOPF,SteadyUACPF,QuasiDynamicACPF,QuasiDynamicACOPF,QuasiDynamicUACPF | FALSE
PMINPRCDEF | DefMinActivePowerPenPrice | Default penalty price for exceeding the minimum active power (PMIN). The default event defined at the network level can be overwritten by a PMINPRC event at the scenario level. Penalty is calculated as (PMIN-P) * PMINPRCDEF | NRGPRC | ∞ [$/MWh] | DCUCOPF,SteadyACOPF,QuasiDynamicACOPF | FALSE
PSETDEF | DefActivePowerSetPoint | Default total active power set point. PSET is equal to PSETDEF if no PSET event is defined for a scenario | PPOW | 0 [MW] | SteadyACPF,SteadyUACPF,QuasiDynamicACPF,QuasiDynamicUACPF | FALSE
PSETPRCDEF | DefActivePowerSetpointPenPrice | Default penalty price for not meeting (curtailing) active power set point (PSETDEF). PSETPRC is equal to PSETPRCDEF if no PSETPRC event is defined for a scenario. Penalty is calculated as (PSET-P) * PSETPRC | NRGPRC | 2000 [$/MWh] | DCUCOPF,SteadyACOPF,QuasiDynamicACOPF | FALSE
QMAXDEF | DefMaxReactivePower | Default maximum reactive power | QPOW | ∞ [MVAr] | SteadyACPF,SteadyACOPF,SteadyUACPF,QuasiDynamicACPF,QuasiDynamicACOPF,QuasiDynamicUACPF | FALSE
QMINDEF | DefMinReactivePower | Default minimum reactive power | QPOW | -∞ [MVAr] | SteadyACPF,SteadyACOPF,SteadyUACPF,QuasiDynamicACPF,QuasiDynamicACOPF,QuasiDynamicUACPF | FALSE
RATEDS | RatedApparentPower | Rated apparent power, assuming balanced three-phase object. If its value is NaN, which is the default, the network Base Apparent Power will be taken. It is used in the network per unit calculations. To change the value of a property to its default, right-click on the property and select “Set to the default value" | SPOW | NaN [MVA] | SteadyUACPF,QuasiDynamicUACPF | FALSE
RATEDV | RatedVoltage | Rated line-to-line voltage, assuming balanced three-phase object. If its value is NaN, which is the default, the network Base Voltage will be taken. It is used in the network per unit calculations. To change the value of a property to its default, right-click on the property and select “Set to the default value" | VOLT | NaN [kV] | DCUCOPF,SteadyACPF,SteadyACOPF,SteadyUACPF,QuasiDynamicACPF,QuasiDynamicACOPF,QuasiDynamicUACPF | FALSE
RRN | PerUnitNeutralResistance | Neutral resistance in pu in the generator base system | PU | 0 [pu] | SteadyUACPF,QuasiDynamicUACPF | FALSE
RRSE | PerUnitOutputResistance | Per phase output resistance in pu in the generator base system | PU | 0 [pu] | SteadyUACPF,QuasiDynamicUACPF | FALSE
Visible | Visible | If true, the object symbol will be visible in maps | NO | True |  | FALSE
VMSETDEF | DefVoltageMagSetPoint | Default voltage magnitude set point | PU | 1 [pu] | SteadyACPF,SteadyACOPF,SteadyUACPF,QuasiDynamicACPF,QuasiDynamicACOPF,QuasiDynamicUACPF | FALSE
VOMPriceDef | DefVOMPrice | Default variable operational and maintenance price per produced energy. VOMPrice property is equal to VOMPriceDef if no VOMPrice event is defined for a scenario | NRGPRC | 0 [$/MWh] | DCUCOPF,SteadyACOPF,QuasiDynamicACOPF | FALSE
XXN | PerUnitNeutralReactance | Neutral reactance in in pu in the generator base system | PU | 0 [pu] | SteadyUACPF,QuasiDynamicUACPF | FALSE
XXSE | PerUnitOutputReactance | Per phase output reactance in in pu in the generator base system | PU | 0 [pu] | SteadyUACPF,QuasiDynamicUACPF | FALSE
PHSTR | Pumped Hydro Storage | Models a pumped hydro storage.
Name | Name | Object Name. Permitted characters are letters, numbers, and underscore ("_"). The name should start with a letter, and have a length of 1 to 30 characters. The name should be unique for each object type |  |  |  | TRUE
NodeName | NodeName | Name of node the external is connected to |  |  |  | TRUE
PlantName | HydroPlantName | Name of the hydro power plant the generator belongs to | NO |  |  | TRUE
Alias | Alias | Alternative object name. Any character, including non-alphanumeric, is allowed |  |  |  | FALSE
C0DEF | DefConstCostCoeff | Default constant coefficient of operational cost | C | 0 [$] | SteadyACOPF,QuasiDynamicACOPF | FALSE
C1DEF | DefLinCostCoeff | Default linear coefficient of operational cost | NRGPRC | 0 [$/MWh] | SteadyACOPF,QuasiDynamicACOPF | FALSE
C2DEF | DefQuadCostCoeff | Default quadratic coefficient of operational cost | NRG2PRC | 0 [$/MWh²] | SteadyACOPF,QuasiDynamicACOPF | FALSE
Info | Info | Information entered for the object. Any character, including non-alphanumeric, is allowed |  |  |  | FALSE
InService | InService | Indicates if an object is considered or disregarded in the execution of a scenario. Externals connected to the node inherit the "inService" status of the node |  | True |  | FALSE
MaxDownRampDef | DefMaxDownRamp | Default maximum downward ramp rate for active power. It describes the rate at which the active power can decrease between two consecutive time steps. It defines the maximum rate of change (decrease) of the object between two consecutives timesteps. MaxDownRamp property is equal to MaxDownRampDef if no MaxDownRamp event is defined for a scenario | RAMP | ∞ [MW/min] | DCUCOPF | FALSE
MaxUpRampDef | DefMaxUpRamp | Default maximum upward ramp rate for active power. It describes the rate at which the active power can increase between two consecutive time steps. It defines the maximum rate of change (increase) of the object between two consecutives timesteps. MaxUpRamp property is equal to MaxUpRampDef if no MaxUpRamp event is defined for a scenario | RAMP | ∞ [MW/min] | DCUCOPF | FALSE
MinDownTimeDDDef | DefMinDownTimeDD | Default minimum down time between consecutive pumping operations | TIME | 0 [h] | DCUCOPF | FALSE
MinDownTimeDGDef | DefMinDownTimeDG | Default minimum down time between consecutive pumping-generating operations | TIME | 0 [h] | DCUCOPF | FALSE
MinDownTimeGDDef | DefMinDownTimeGD | Default minimum down time between consecutive generating-pumping operations | TIME | 0 [h] | DCUCOPF | FALSE
MinDownTimeGGDef | DefMinDownTimeGG | Default minimum down time between consecutive generating operations | TIME | 0 [h] | DCUCOPF | FALSE
MinUpTimeDDef | DefMinUpTimeD | Default minimum up time for pumping operation | TIME | 0 [h] | DCUCOPF | FALSE
MinUpTimeGDef | DefMinUpTimeG | Default minimum up time for generating operation | TIME | 0 [h] | DCUCOPF | FALSE
PDCOEFF | FlowToPowerDemandCoeff | Active power consumption per volumetric flow rate pumped by hydro pump | POWQVOL | 0 [MW/m³/s] | DCUCOPF | FALSE
PDMAXDEF | DefMaxPumpDemandPower | Default max demand rate for pumping | PPOW | ∞ [MW] | DCUCOPF,SteadyACPF,SteadyACOPF,SteadyUACPF,QuasiDynamicACPF,QuasiDynamicACOPF,QuasiDynamicUACPF | FALSE
PDMAXPRCDEF | DefMaxPumpPowerPenPrice | Default penalty price for max demand rate for pumping | NRGPRC | ∞ [$/MWh] | SteadyACOPF,QuasiDynamicACOPF | FALSE
PDMINDEF | DefMinPumpDemandPower | Default min demand rate for pumping | PPOW | 0 [MW] | DCUCOPF,SteadyACPF,SteadyACOPF,SteadyUACPF,QuasiDynamicACPF,QuasiDynamicACOPF,QuasiDynamicUACPF | FALSE
PDMINPRCDEF | DefMinPumpPowerPenPrice | Default penalty price for min demand rate for pumping | NRGPRC | ∞ [$/MWh] | SteadyACOPF,QuasiDynamicACOPF | FALSE
PFSETDEF | DefActivePowerCompensationFactor | Default active power slack participation factor set point (does not apply in DCUCOPF). If participation factors are not provided (=0), slack will be distributed according to generator size | ND | 0 | SteadyACPF,SteadyUACPF,QuasiDynamicACPF,QuasiDynamicUACPF | FALSE
PGCOEFF | FlowToPowerGenerationCoeff | Active power generation per volumetric flow rate driving hydro turbine | POWQVOL | 0 [MW/m³/s] | DCUCOPF | FALSE
PGMAXDEF | DefMaxTurbGenerationPower | Default max generation rate by turbination | PPOW | ∞ [MW] | DCUCOPF,SteadyACPF,SteadyACOPF,SteadyUACPF,QuasiDynamicACPF,QuasiDynamicACOPF,QuasiDynamicUACPF | FALSE
PGMAXPRCDEF | DefMaxTurbPowerPenPrice | Default penalty price for max generation rate by turbination | NRGPRC | ∞ [$/MWh] | SteadyACOPF,QuasiDynamicACOPF | FALSE
PGMINDEF | DefMinTurbGenerationPower | Default min generation rate by turbination | PPOW | 0 [MW] | DCUCOPF,SteadyACPF,SteadyACOPF,SteadyUACPF,QuasiDynamicACPF,QuasiDynamicACOPF,QuasiDynamicUACPF | FALSE
PGMINPRCDEF | DefMinTurbPowerPenPrice | Default penalty price for min generation rate by turbination | NRGPRC | ∞ [$/MWh] | SteadyACOPF,QuasiDynamicACOPF | FALSE
PSETDEF | DefActivePowerSetPoint | Default total active power set point. PSET is equal to PSETDEF if no PSET event is defined for a scenario | PPOW | 0 [MW] | SteadyACPF,SteadyUACPF,QuasiDynamicACPF,QuasiDynamicUACPF | FALSE
PSETPRCDEF | DefActivePowerSetpointPenPrice | Default penalty price for not meeting (curtailing) active power set point (PSETDEF). PSETPRC is equal to PSETPRCDEF if no PSETPRC event is defined for a scenario. Penalty is calculated as (PSET-P) * PSETPRC | NRGPRC | 2000 [$/MWh] | DCUCOPF,SteadyACOPF,QuasiDynamicACOPF | FALSE
QMAXDEF | DefMaxReactivePower | Default maximum reactive power | QPOW | ∞ [MVAr] | SteadyACPF,SteadyACOPF,SteadyUACPF,QuasiDynamicACPF,QuasiDynamicACOPF,QuasiDynamicUACPF | FALSE
QMINDEF | DefMinReactivePower | Default minimum reactive power | QPOW | -∞ [MVAr] | SteadyACPF,SteadyACOPF,SteadyUACPF,QuasiDynamicACPF,QuasiDynamicACOPF,QuasiDynamicUACPF | FALSE
Visible | Visible | If true, the object symbol will be visible in maps | NO | True |  | FALSE
VMSETDEF | DefVoltageMagSetPoint | Default voltage magnitude set point | PU | 1 [pu] | SteadyACPF,SteadyACOPF,SteadyUACPF,QuasiDynamicACPF,QuasiDynamicACOPF,QuasiDynamicUACPF | FALSE
VOMDPriceDef | DefVOMDPrice | Default variable operational and maintenance cost per stored/charged energy | NRGPRC | 0 [$/MWh] | DCUCOPF,SteadyACOPF,QuasiDynamicACOPF | FALSE
VOMGPriceDef | DefVOMGPrice | Default variable operational and maintenance cost per generated/discharged energy | NRGPRC | 0 [$/MWh] | DCUCOPF,SteadyACOPF,QuasiDynamicACOPF | FALSE
FUEL | Fuel | Models the consumption and emission of the fuel used by one or more fuel generators
Name | Name | Object Name. Permitted characters are letters, numbers, and underscore ("_"). The name should start with a letter, and have a length of 1 to 30 characters. The name should be unique for each object type |  |  |  | TRUE
Alias | Alias | Alternative object name. Any character, including non-alphanumeric, is allowed |  |  |  | FALSE
CO2 | CO2EmissionPerFuelUnit | CO2 emission per fuel unit | NO | 0 | DCUCOPF | FALSE
FuelPriceDef | DefFuelPrice | Default fuel price | NO | 0 | DCUCOPF | FALSE
FuelUnit | FuelUnit | Fuel unit of specified fuel unit type |  | [m³] | DCUCOPF,SteadyACPF,SteadyACOPF,SteadyUACPF,QuasiDynamicACPF,QuasiDynamicACOPF,QuasiDynamicUACPF | FALSE
Info | Info | Information entered for the object. Any character, including non-alphanumeric, is allowed |  |  |  | FALSE
InService | InService | Indicates if an object is considered or disregarded in the execution of a scenario. Externals connected to the node inherit the "inService" status of the node |  | True |  | FALSE
NOX | NOXEmissionPerFuelUnit | NOx emission per fuel unit | NO | 0 | DCUCOPF | FALSE
SO2 | SO2EmissionPerFuelUnit | SO2 emission per fuel unit | NO | 0 | DCUCOPF | FALSE
FGEN | Fuel Generator | Models the injection of electric power by a fuel generator that generates electricity by converting chemical energy stored in a fuel first into mechanical energy and then into electrical energy. A fuel generator requires a fuel object (oil, gas, coal, nuclear, etc.) for operation
Name | Name | Object Name. Permitted characters are letters, numbers, and underscore ("_"). The name should start with a letter, and have a length of 1 to 30 characters. The name should be unique for each object type |  |  |  | TRUE
FuelName | FuelName | Name of fuel the generator consumes | NO |  |  | TRUE
NodeName | NodeName | Name of node the external is connected to |  |  |  | TRUE
Alias | Alias | Alternative object name. Any character, including non-alphanumeric, is allowed |  |  |  | FALSE
C0DEF | DefConstCostCoeff | Default constant coefficient of operational cost | C | 0 [$] | SteadyACOPF,QuasiDynamicACOPF | FALSE
C1DEF | DefLinCostCoeff | Default linear coefficient of operational cost | NRGPRC | 0 [$/MWh] | SteadyACOPF,QuasiDynamicACOPF | FALSE
C2DEF | DefQuadCostCoeff | Default quadratic coefficient of operational cost | NRG2PRC | 0 [$/MWh²] | SteadyACOPF,QuasiDynamicACOPF | FALSE
CALCDFLT | CalcDefault | Calculate default values for maximum ramp rate (MaxUpRampDef and MaxDownRampDef), and (when applicable) startup time (MinUpTimeDef and MinDownTimeDef), generator capability curve (GCC), heat rate curve (HR0, HR1, and HR2) |  | SELECT | DCUCOPF,SteadyACPF,SteadyACOPF,SteadyUACPF,QuasiDynamicACPF,QuasiDynamicACOPF,QuasiDynamicUACPF | FALSE
EFFMAX | MaxThermalEfficiency | Maximum thermal efficiency of the generator | ND | 0.7 | SteadyACPF,SteadyACOPF,QuasiDynamicACPF,QuasiDynamicACOPF | FALSE
EFFMIN | MinThermalEfficiency | Minimum thermal efficiency of the generator | ND | 0.24 | SteadyACPF,SteadyACOPF,QuasiDynamicACPF,QuasiDynamicACOPF | FALSE
FC0 | ConstFuelConsCoeff | Constant fuel consumption coefficient | NO | 0 | DCUCOPF | FALSE
FC1 | LinFuelConsCoeff | Linear fuel consumption coefficient | NO | 0 | DCUCOPF | FALSE
FC2 | QuadFuelConsCoeff | Quadratic fuel consumption coefficient | NO | 0 | DCUCOPF | FALSE
GenType | GeneratorType | Specifies the generator type | NO | GASTURBINE |  | FALSE
HR0 | ConstHeatRateCoeff | Constant heat rate coefficient | HR | 0 [MJ/kWh] | SteadyACPF,SteadyACOPF,QuasiDynamicACPF,QuasiDynamicACOPF | FALSE
HR1 | LinHeatRateCoeff | Linear heat rate coefficient | POWHR | 0 [MJ/kWh/MW] | SteadyACPF,SteadyACOPF,QuasiDynamicACPF,QuasiDynamicACOPF | FALSE
HR2 | QuadHeatRateCoeff | Quadratic heat rate coefficient | POW2HR | 0 [MJ/kWh/MW²] | SteadyACPF,SteadyACOPF,QuasiDynamicACPF,QuasiDynamicACOPF | FALSE
Info | Info | Information entered for the object. Any character, including non-alphanumeric, is allowed |  |  |  | FALSE
InService | InService | Indicates if an object is considered or disregarded in the execution of a scenario. Externals connected to the node inherit the "inService" status of the node |  | True |  | FALSE
MaxDownRampDef | DefMaxDownRamp | Default maximum downward ramp rate for active power. It describes the rate at which the active power can decrease between two consecutive time steps. It defines the maximum rate of change (decrease) of the object between two consecutives timesteps. MaxDownRamp property is equal to MaxDownRampDef if no MaxDownRamp event is defined for a scenario | RAMP | ∞ [MW/min] | DCUCOPF | FALSE
MaxUpRampDef | DefMaxUpRamp | Default maximum upward ramp rate for active power. It describes the rate at which the active power can increase between two consecutive time steps. It defines the maximum rate of change (increase) of the object between two consecutives timesteps. MaxUpRamp property is equal to MaxUpRampDef if no MaxUpRamp event is defined for a scenario | RAMP | ∞ [MW/min] | DCUCOPF | FALSE
MinDownTimeDef | DefMinDownTime | Default minimum down time, i.e. minimum duration a generator must be offline before it can start up. MinDownTime property is equal to MinDownTimeDef if no MinDownTime event is defined for a scenario | TIME | 0 [h] | DCUCOPF | FALSE
MinUpTimeDef | DefMinUpTime | Default minimum up time, i.e. minimum duration a generator must be online before it can shut down. MinUpTime property is equal to MinUpTimeDef if no MinUpTime event is defined for a scenario | TIME | 0 [h] | DCUCOPF | FALSE
NSEG | NumOfPieceWiseLinearSegments | Specifies the number of piece-wise-linear segments quadratic fuel consumption curve will be divided into. Range 2 to 6. First segment represents line ranging from P=0 to P=PMIN | ND | 2 | DCUCOPF | FALSE
PFSETDEF | DefActivePowerCompensationFactor | Default active power slack participation factor set point (does not apply in DCUCOPF). If participation factors are not provided (=0), slack will be distributed according to generator size | ND | 0 | SteadyACPF,SteadyUACPF,QuasiDynamicACPF,QuasiDynamicUACPF | FALSE
PMAXDEF | DefMaxActivePower | Default maximum active power also used to calculate name plate capacity (NCAP). PMAX property is equal to PMAXDEF if no PMAX event is defined for a scenario | PPOW | ∞ [MW] | DCUCOPF,SteadyACPF,SteadyACOPF,SteadyUACPF,QuasiDynamicACPF,QuasiDynamicACOPF,QuasiDynamicUACPF | FALSE
PMAXPRCDEF | DefMaxActivePowerPenPrice | Default penalty price for exceeding the maximum active power (PMAX). The default event defined at the network level can be overwritten by a PMAXPRC event at the scenario level. Penalty is calculated as (P-PMAX) * PMAXPRCDEF | NRGPRC | ∞ [$/MWh] | SteadyACOPF,QuasiDynamicACOPF | FALSE
PMINDEF | DefMinActivePower | Default minimum active power. PMIN property is equal to PMINDEF if no PMIN event is defined for a scenario | PPOW | 0 [MW] | DCUCOPF,SteadyACPF,SteadyACOPF,SteadyUACPF,QuasiDynamicACPF,QuasiDynamicACOPF,QuasiDynamicUACPF | FALSE
PMINPRCDEF | DefMinActivePowerPenPrice | Default penalty price for exceeding the minimum active power (PMIN). The default event defined at the network level can be overwritten by a PMINPRC event at the scenario level. Penalty is calculated as (PMIN-P) * PMINPRCDEF | NRGPRC | ∞ [$/MWh] | SteadyACOPF,QuasiDynamicACOPF | FALSE
PSETDEF | DefActivePowerSetPoint | Default total active power set point. PSET is equal to PSETDEF if no PSET event is defined for a scenario | PPOW | 0 [MW] | SteadyACPF,SteadyUACPF,QuasiDynamicACPF,QuasiDynamicUACPF | FALSE
PSETPRCDEF | DefActivePowerSetpointPenPrice | Default penalty price for not meeting (curtailing) active power set point (PSETDEF). PSETPRC is equal to PSETPRCDEF if no PSETPRC event is defined for a scenario. Penalty is calculated as (PSET-P) * PSETPRC | NRGPRC | 2000 [$/MWh] | DCUCOPF,SteadyACOPF,QuasiDynamicACOPF | FALSE
QMAXDEF | DefMaxReactivePower | Default maximum reactive power | QPOW | ∞ [MVAr] | SteadyACPF,SteadyACOPF,SteadyUACPF,QuasiDynamicACPF,QuasiDynamicACOPF,QuasiDynamicUACPF | FALSE
QMINDEF | DefMinReactivePower | Default minimum reactive power | QPOW | -∞ [MVAr] | SteadyACPF,SteadyACOPF,SteadyUACPF,QuasiDynamicACPF,QuasiDynamicACOPF,QuasiDynamicUACPF | FALSE
RATEDS | RatedApparentPower | Rated apparent power, assuming balanced three-phase object. If its value is NaN, which is the default, the network Base Apparent Power will be taken. It is used in the network per unit calculations. To change the value of a property to its default, right-click on the property and select “Set to the default value" | SPOW | NaN [MVA] | SteadyUACPF,QuasiDynamicUACPF | FALSE
RATEDV | RatedVoltage | Rated line-to-line voltage, assuming balanced three-phase object. If its value is NaN, which is the default, the network Base Voltage will be taken. It is used in the network per unit calculations. To change the value of a property to its default, right-click on the property and select “Set to the default value" | VOLT | NaN [kV] | DCUCOPF,SteadyACPF,SteadyACOPF,SteadyUACPF,QuasiDynamicACPF,QuasiDynamicACOPF,QuasiDynamicUACPF | FALSE
RRN | PerUnitNeutralResistance | Neutral resistance in pu in the generator base system | PU | 0 [pu] | SteadyUACPF,QuasiDynamicUACPF | FALSE
RRSE | PerUnitOutputResistance | Per phase output resistance in pu in the generator base system | PU | 0 [pu] | SteadyUACPF,QuasiDynamicUACPF | FALSE
ShutDownPriceDef | DefShutDownPrice | Default price for shutting down a generator. ShutDownPrice property is equal to ShutDownPriceDef if no ShutDownPrice event is defined for a scenario | C | 0 [$] | DCUCOPF | FALSE
StartUpPriceDef | DefStartUpPrice | Default price for starting up a generator. StartUpPrice property is equal to StartUpPriceDef if no StartUpPrice event is defined for a scenario | C | 0 [$] | DCUCOPF | FALSE
Visible | Visible | If true, the object symbol will be visible in maps | NO | True |  | FALSE
VMSETDEF | DefVoltageMagSetPoint | Default voltage magnitude set point | PU | 1 [pu] | SteadyACPF,SteadyACOPF,SteadyUACPF,QuasiDynamicACPF,QuasiDynamicACOPF,QuasiDynamicUACPF | FALSE
VOMPriceDef | DefVOMPrice | Default variable operational and maintenance price per produced energy. VOMPrice property is equal to VOMPriceDef if no VOMPrice event is defined for a scenario | NRGPRC | 0 [$/MWh] | DCUCOPF,SteadyACOPF,QuasiDynamicACOPF | FALSE
XXN | PerUnitNeutralReactance | Neutral reactance in in pu in the generator base system | PU | 0 [pu] | SteadyUACPF,QuasiDynamicUACPF | FALSE
XXSE | PerUnitOutputReactance | Per phase output reactance in in pu in the generator base system | PU | 0 [pu] | SteadyUACPF,QuasiDynamicUACPF | FALSE
ASVC | Ancillary Service | Models the ability of generators and demands to provide reserve capacity (upward or downward reserve) to the electric network in case of an unexpected contingency
Name | Name | Object Name. Permitted characters are letters, numbers, and underscore ("_"). The name should start with a letter, and have a length of 1 to 30 characters. The name should be unique for each object type |  |  |  | TRUE
Alias | Alias | Alternative object name. Any character, including non-alphanumeric, is allowed |  |  |  | FALSE
ASVCType | AncillayServiceType | Type of ancillary service |  | UpReserve | DCUCOPF | FALSE
Unit | AncillayServiceUnit | Unit to be used for ancillary service |  | [MW] | DCUCOPF | FALSE
Info | Info | Information entered for the object. Any character, including non-alphanumeric, is allowed |  |  |  | FALSE
InService | InService | Indicates if an object is considered or disregarded in the execution of a scenario. Externals connected to the node inherit the "inService" status of the node |  | True |  | FALSE
MinValDef | DefMinServiceValue | Default minimum ancillary service requirement value | NO | 0 | DCUCOPF | FALSE
MinValPriceDef | DefMinValPenPrice | Default penalty price for not meeting minimum ancillary service requirement | NO | 0 | DCUCOPF | FALSE
ASVCX | Ancillary Service External | Models the facilities contributing to an ancillary service
Name | Name | Object Name. Permitted characters are letters, numbers, and underscore ("_"). The name should start with a letter, and have a length of 1 to 30 characters. The name should be unique for each object type |  |  |  | TRUE
Alias | Alias | Alternative object name. Any character, including non-alphanumeric, is allowed |  |  |  | FALSE
ASVCPriceDef | DefAncillaryServicePrice | Default price for contributing to ancillary service | NO | 0 | DCUCOPF | FALSE
Info | Info | Information entered for the object. Any character, including non-alphanumeric, is allowed |  |  |  | FALSE
InService | InService | Indicates if an object is considered or disregarded in the execution of a scenario. Externals connected to the node inherit the "inService" status of the node |  | True |  | FALSE
MaxValDef | DefMaxContribToService | Default maximum contribution to service by the external | NO | 0 | DCUCOPF | FALSE
ASVCName | AncillaryService | Ancillary service the external is contributing to |  |  |  | FALSE
ECNSTR | Electric Constraint | Models a user-defined linear equality or inequality constraint describing relations between the variables of different electric objects
Name | Name | Object Name. Permitted characters are letters, numbers, and underscore ("_"). The name should start with a letter, and have a length of 1 to 30 characters. The name should be unique for each object type |  |  |  | TRUE
Alias | Alias | Alternative object name. Any character, including non-alphanumeric, is allowed |  |  |  | FALSE
AvgLowBoundDef | DefAvgLowerBound | Default time averaged lower bound of constraint | ND | -∞ | DCUCOPF,SteadyACPF,SteadyACOPF,SteadyUACPF,QuasiDynamicACPF,QuasiDynamicACOPF,QuasiDynamicUACPF | FALSE
AvgUpBoundDef | DefAvgUpperBound | Default time averaged upper bound of constraint | ND | ∞ | DCUCOPF,SteadyACPF,SteadyACOPF,SteadyUACPF,QuasiDynamicACPF,QuasiDynamicACOPF,QuasiDynamicUACPF | FALSE
Info | Info | Information entered for the object. Any character, including non-alphanumeric, is allowed |  |  |  | FALSE
InService | InService | Indicates if an object is considered or disregarded in the execution of a scenario. Externals connected to the node inherit the "inService" status of the node |  | True |  | FALSE
LowBoundDef | DefLowerBound | Default lower bound of constraint | ND | -∞ | DCUCOPF,SteadyACPF,SteadyACOPF,SteadyUACPF,QuasiDynamicACPF,QuasiDynamicACOPF,QuasiDynamicUACPF | FALSE
UpBoundDef | DefUpperBound | Default upper bound of constraint | ND | ∞ | DCUCOPF,SteadyACPF,SteadyACOPF,SteadyUACPF,QuasiDynamicACPF,QuasiDynamicACOPF,QuasiDynamicUACPF | FALSE
EVAR | Electric Variable | Models a variable of an electric object and its corresponding coefficient utilized in a user-defined constraint
Name | Name | Object Name. Permitted characters are letters, numbers, and underscore ("_"). The name should start with a letter, and have a length of 1 to 30 characters. The name should be unique for each object type |  |  |  | TRUE
Alias | Alias | Alternative object name. Any character, including non-alphanumeric, is allowed |  |  |  | FALSE
CoeffDef | DefCoefficient | Default coefficient for object variable | ND | 1 | DCUCOPF,SteadyACPF,SteadyACOPF,SteadyUACPF,QuasiDynamicACPF,QuasiDynamicACOPF,QuasiDynamicUACPF | FALSE
Info | Info | Information entered for the object. Any character, including non-alphanumeric, is allowed |  |  |  | FALSE
InService | InService | Indicates if an object is considered or disregarded in the execution of a scenario. Externals connected to the node inherit the "inService" status of the node |  | False |  | FALSE
ObjVarName | ObjectVariableName | Name of object variable |  | NONE |  | FALSE
Unit | ObjectVariableUnit | Unit for object variable |  |  |  | FALSE
CNSTRName | Constraint | Constraint the variable is referring to |  |  |  | FALSE
NetObjID | NetObject | Network object the variable is referring to |  |  |  | FALSE
NetObjID | NetObjectID | ID of Network Object the variable is referring to |  |  |  | FALSE
POLY | Branch Vertices | Models the curvature of a branch using internal points called branch vertices
EBR.<ObjName> |  | Info: EBR is the object type code for all electric branches, however, more specific object type codes can used as well (.e.g. LI, TRF)
X-CoordinateOfVertex_1 | Y-CoordinateOfVertex_1
X-CoordinateOfVertex_2 | Y-CoordinateOfVertex_2
X-CoordinateOfVertex_3 | Y-CoordinateOfVertex_3
⋮
X-CoordinateOfVertex_4 | Y-CoordinateOfVertex_4
#
EGRPM | Members of Electric Group | Models the members of electric groups
[GRPM] | <NameOfElectricGroup>
NameOfElectricGroupMember_1
NameOfElectricGroupMember_2
NameOfElectricGroupMember_3
⋮
NameOfElectricGroupMember_4

## UNITINFO
Unit | Description | Alias
NO | State
No Unit
ND | Dimensionless
[-] | Dimensionless
PC | PerCent
[%] | PerCent
L | Length
[μm] | Micro meter | [um]
[mm] | Milli meter
[cm] | Centi meter
[km] | Kilo meter
[in] | Inch
[ft] | Feet
[mi] | Miles
[m] | Meter
H | Elevation
[μm] | Micro meter | [um]
[mm] | Milli meter
[cm] | Centi meter
[km] | Kilo meter
[in] | Inch
[ft] | Feet
[mi] | Miles
[m] | Meter
XY | XY-Coordinate
[μm] | Micro meter | [um]
[mm] | Milli meter
[cm] | Centi meter
[km] | Kilo meter
[in] | Inch
[ft] | Feet
[mi] | Miles
[m] | Meter
LATLONG | Geographic Coordinates
[°] | Degrees | [deg]
[-] | Dimensionless
VOL | Volume
[L] | Liter
[ft³] | Cubic feet | [ft3]
[gal] | Gallon
[usgal] | US Gallon
[hm³] | Cubic Hecto Meter | [hm3]
[m³] | Cubic meter | [m3]
TIME | Time
[wk] | Week
[d] | Day
[h] | Hour
[min] | Minute
[s] | Second
ANGLE | Angle
[rad] | Radians
[°] | Degrees | [deg]
PU | PerUnit
[pu] | Per unit
VOLT | Voltage
[V] | Volt
[MV] | Megavolt
[kV] | Kilovolt
CURR | Current
[mA] | Milliampere
[kA] | Kiloampere
[A] | Ampere
PPOW | Active power
[W] | Watt
[kW] | Kilowatt
[GW] | Gigawatt
[TW] | Terawatt
[MW] | Megawatt
QPOW | Reactive power
[VAr] | Mega volt ampere reactive
[kVAr] | Mega volt ampere reactive
[MVAr] | Mega volt ampere reactive
SPOW | Apparent power
[VA] | Volt ampere
[kVA] | Kilo volt ampere
[MVA] | Mega volt ampere
HR | Heat rate
[Btu/kWh] | British Thermal Unit per Kilo Watt Hour | [btu/kWh]
[J/kWh] | Joule per kilowatt hour
[kJ/kWh] | Kilo Joule per Kilo Watt Hour
[MMBTU/MWh] | Millions of British Thermal Unit per Mega Watt Hour | [MMbtu/MWh], [mmbtu/MWh]
[MJ/kWh] | Megajoule per kilowatt hour
RAMP | Ramp rate
[W/s] | Watt per second
[W/min] | Watt per minute
[W/h] | Watt per hour
[kW/s] | Kilo Watt per second
[kW/min] | Kilo Watt per minute
[kW/h] | Kilo Watt per hour
[MW/s] | Mega Watt per second
[MW/min] | Mega Watt per minute
[MW/h] | Mega Watt per hour
RRL | Resistance per Length
[Ω/m] | Ohm per Meter | [O/m]
[Ω/km] | Ohm per Kilo Meter | [O/km]
[Ω/ft] | Ohm per Feet | [O/ft]
[Ω/mi] | Ohm per Mile | [O/mi]
[mΩ/m] | Milli Ohm per Meter | [mO/m]
[mΩ/km] | Milli Ohm per Kilo Meter | [mO/km]
[mΩ/ft] | Milli Ohm per Feet | [mO/ft]
[mΩ/mi] | Milli Ohm per Mile | [mO/mi]
[kΩ/m] | Kilo Ohm per Meter | [kO/m]
[kΩ/km] | Kilo Ohm per Kilo Meter | [kO/km]
[kΩ/ft] | Kilo Ohm per Feet | [kO/ft]
[kΩ/mi] | Kilo Ohm per Mile | [kO/mi]
GGL | Conductance per Length
[S/m] | Siemens per Meter
[S/km] | Siemens per Kilo Meter
[S/ft] | Siemens per Feet
[S/mi] | Siemens per Mile
[mS/m] | Milli Siemens per Meter
[mS/km] | Milli Siemens per Kilo Meter
[mS/ft] | Milli Siemens per Feet
[mS/mi] | Milli Siemens per Mile
[μS/m] | Micro Siemens per Meter | [uS/m]
[μS/km] | Micro Siemensd per Kilo Meter | [uS/km]
[μS/ft] | Micro Siemens per Feet | [uS/ft]
[μS/mi] | Micro Siemens per Mile | [uS/mi]
[nS/m] | Nano Siemens per Meter
[nS/km] | Nano Siemens per Kilo Meter
[nS/ft] | Nano Siemens per Feet
[nS/mi] | Nano Siemens per Mile
FRQ | Frequency
[Hz] | Hertz
[kHz] | Kilo Hertz
[MHz] | Mega Hertz
[GHz] | Giga Hertz
NRG | Energy
[J] | Joule
[kJ] | Kilo Joule
[MJ] | Mega Joule
[kWh] | Kilo Watt hour
[MWh] | Mega Watt hour
[GWh] | Giga Watt hour
[Btu] | British thermal unit | [BTU], [btu]
[MBTU] | Thousands of British Thermal Unit | [MBtu], [Mbtu]
[MMBTU] | Millions of British Thermal Unit | [MMBtu], [MMbtu]
POWQVOL | Active Power per Volumetric Flow
[MW/m³/s] | Mega Watts per Cubic Meter per Second | [MW/m3/s]
[MW/L/s] | Mega Watts per Liters per Second
[MW/ft³/s] | Mega Watts per Cubic Feet per Second | [MW/ft3/s]
[MW/gal/s] | Mega Watts per Imperial Gallon per Second
[MW/usgal/s] | Mega Watts per US Gallon per Second
POWHR | Heat Rate per Active Power
[MJ/kWh/MW] | Mega Joule per Kilo Watt Hour per Mega Watt
[kJ/kWh/MW] | Kilo Joule per Kilo Watt Hour per Mega Watt
[J/kWh/MW] | Joule per Kilo Watt Hour per Mega Watt
[BTU/kWh/MW] | British Thermal Unit per Kilo Watt Hour per Mega Watt | [Btu/kWh/MW], [btu/kWh/MW]
[MBTU/kWh/MW] | Thousands of British Thermal Unit per Kilo Watt Hour per Mega Watt | [MBtu/kWh/MW], [mbtu/kWh/MW]
[MMBTU/MWh/MW] | Millions of British Thermal Unit per Mega Watt Hour per Mega Watt | [MMbtu/MWh/MW], [mmbtu/MWh/MW]
[MMBTU/kWh/MW] | Millions of British Thermal Unit per Kilo Watt Hour per Mega Watt | [MMBtu/kWh/MW], [mmbtu/kWh/MW]
POW2HR | Heat Rate per Active Power Square
[MJ/kWh/MW²] | Mega Joule per Kilo Watt Hour per Mega Watt Square | [MJ/kWh/MW2]
[kJ/kWh/MW²] | Kilo Joule per Kilo Watt Hour per Mega Watt Square | [kJ/kWh/MW2]
[J/kWh/MW²] | Joule per Kilo Watt Hour per Mega Watt Square | [J/kWh/MW2]
[BTU/kWh/MW²] | British Thermal Unit per Kilo Watt Hour per Mega Watt Square | [Btu/kWh/MW²], [btu/kWh/MW²], [BTU/kWh/MW2], [Btu/kWh/MW2], [btu/kWh/MW2]
[MBTU/kWh/MW²] | Thousands of British Thermal Unit per Kilo Watt Hour per Mega Watt Square | [MBtu/kWh/MW²], [mbtu/kWh/MW²], [MBTU/kWh/MW2], [MBtu/kWh/MW2], [mbtu/kWh/MW2]
[MMBTU/MWh/MW²] | Millions of British Thermal Unit per Mega Watt Hour per Mega Watt Square | [MMBtu/MWh/MW²], [mmbtu/MWh/MW²], [MMBTU/MWh/MW2], [MMBtu/MWh/MW2], [mmbtu/MWh/MW2]
[MMBTU/kWh/MW²] | Millions of British Thermal Unit per Kilo Watt Hour per Mega Watt Square | [MMBtu/kWh/MW²], [mmbtu/kWh/MW²], [MMBTU/kWh/MW2], [MMBtu/kWh/MW2], [mmbtu/kWh/MW2]
HQVOL | Volumetric Flow Rate Hydro
[m³/s] | Cubic meter per second | [m3/s]
[m³/h] | Cubic meter per hour | [m3/h]
[m³/d] | Cubic meter per day | [m3/d]
[m³/min] | Cubic meter per minute | [m3/min]
[L/d] | Liters per day
[L/h] | Liters per hour
[L/s] | Liters per second
[L/min] | Liters per minute
[ft³/s] | Cubic feet per second | [ft3/s]
[ft³/h] | Cubic feet per hour | [ft3/h]
[ft³/d] | Cubic Feet per Day | [ft3/d]
[ft³/min] | Cubic Feet per Minute | [ft3/min]
[gal/s] | Imperial Gallon per Second
[gal/h] | Gallon per Hour
[gal/d] | Imperial Gallon per Day
[gal/min] | Imperial Gallon per Minute
[usgal/s] | US Gallon per Second
[usgal/h] | US Gallon per Hour
[usgal/d] | US Gallon per Day
[usgal/min] | US Gallon per Minute
C | Currency
[$] | US Dollar | [usd], [USD]
[€] | Euro | [eur], [EUR]
[£] | British Pound | [gbp], [GBP]
NRGPRC | Price per Energy
[$/kWh] | US Dollar per Kilo Watt Hour | [USD/kWh], [usd/kWh]
[£/kWh] | British Pounds per Kilo Watt Hour | [GBP/kWh], [gbp/kWh]
[€/kWh] | Euro per Kilo Watt Hour | [EUR/kWh], [eur/kWh]
[$/MWh] | US Dollar per Mega Watt Hour | [USD/MWh], [usd/MWh]
[£/MWh] | British Pounds per Mega Watt Hour | [GBP/MWh], [gbp/MWh]
[€/MWh] | Euro per Mega Watt Hour | [EUR/MWh], [eur/MWh]
[$/MJ] | US Dollar per Mega Joule | [USD/MJ], [usd/MJ]
[£/MJ] | British Pounds per Mega Joule | [GBP/MJ], [gbp/MJ]
[€/MJ] | Euro per Mega Joule | [EUR/MJ], [eur/MJ]
[$/kJ] | US Dollar per Kilo Joule | [USD/kJ], [usd/kJ]
[£/kJ] | British Pounds per Kilo Joule | [GBP/kJ], [gbp/kJ]
[€/kJ] | Euro per Kilo Joule | [EUR/kJ], [eur/kJ]
[$/J] | US Dollar per Joule | [USD/J], [usd/J]
[£/J] | British Pounds per Joule | [GBP/J], [gbp/J]
[€/J] | Euro per Joule | [EUR/J], [eur/J]
[$/MMBTU] | US Dollar per Millions of British Thermal Unit | [USD/MMBTU], [usd/MMBTU], [$/MMbtu], [USD/MMbtu], [usd/MMbtu], [$/mmbtu], [USD/mmbtu], [usd/mmbtu]
[£/MMBTU] | British Pounds per Millions of British Thermal Unit | [GBP/MMBTU], [gbp/MMBTU], [£/MMbtu], [GBP/MMbtu], [gbp/MMbtu], [£/mmbtu], [GBP/mmbtu], [gbp/mmbtu]
[€/MMBTU] | Euro per Millions of British Thermal Unit | [EUR/MMBTU], [eur/MMBTU], [€/MMbtu], [EUR/MMbtu], [eur/MMbtu], [€/mmbtu], [EUR/mmbtu], [eur/mmbtu]
[$/MBTU] | US Dollar per Thousands of British Thermal Unit | [USD/MBTU], [usd/MBTU], [$/Mbtu], [USD/Mbtu], [usd/Mbtu], [$/mbtu], [USD/mbtu], [usd/mbtu]
[£/MBTU] | British Pounds per Thousands of British Thermal Unit | [GBP/MBTU], [gbp/MBTU], [£/Mbtu], [GBP/Mbtu], [gbp/Mbtu], [£/mbtu], [GBP/mbtu], [gbp/mbtu]
[€/MBTU] | Euro per Thousands of British Thermal Unit | [EUR/MBTU], [eur/MBTU], [€/Mbtu], [EUR/Mbtu], [eur/Mbtu], [€/mbtu], [EUR/mbtu], [eur/mbtu]
[$/BTU] | US Dollar per British Thermal Unit | [USD/BTU], [usd/BTU], [$/Btu], [USD/Btu], [usd/Btu], [$/btu], [USD/btu], [usd/btu]
[£/BTU] | British Pounds per British Thermal Unit | [GBP/BTU], [gbp/BTU], [£/Btu], [GBP/Btu], [gbp/Btu], [£/btu], [GBP/btu], [gbp/btu]
[€/BTU] | Euro per British Thermal Unit | [EUR/BTU], [eur/BTU], [€/Btu], [EUR/Btu], [eur/Btu], [€/btu], [EUR/btu], [eur/btu]
NRG2PRC | Price per Energy Square
[$/kWh²] | US Dollar per Kilo Watt Hour Square | [USD/kWh²], [usd/kWh²], [$/kWh2], [USD/kWh2], [usd/kWh2]
[£/kWh²] | British Pounds per Kilo Watt Hour Square | [GBP/kWh²], [gbp/kWh²], [£/kWh2], [GBP/kWh2], [gbp/kWh2]
[€/kWh²] | Euro per Kilo Watt Hour Square | [EUR/kWh²], [eur/kWh²], [€/kWh2], [EUR/kWh2], [eur/kWh2]
[$/MWh²] | US Dollar per Mega Watt Hour Square | [USD/MWh²], [usd/MWh²], [$/MWh2], [USD/MWh2], [usd/MWh2]
[£/MWh²] | British Pounds per Mega Watt Hour Square | [GBP/MWh²], [gbp/MWh²], [£/MWh2], [GBP/MWh2], [gbp/MWh2]
[€/MWh²] | Euro per Mega Watt Hour Square | [EUR/MWh²], [eur/MWh²], [€/MWh2], [EUR/MWh2], [eur/MWh2]
[$/MJ²] | US Dollar per Mega Joule Square | [USD/MJ²], [usd/MJ²], [$/MJ2], [USD/MJ2], [usd/MJ2]
[£/MJ²] | British Pounds per Mega Joule Square | [GBP/MJ²], [gbp/MJ²], [£/MJ2], [GBP/MJ2], [gbp/MJ2]
[€/MJ²] | Euro per Mega Joule Square | [EUR/MJ²], [eur/MJ²], [€/MJ2], [EUR/MJ2], [eur/MJ2]
[$/kJ²] | US Dollar per Kilo Joule Square | [USD/kJ²], [usd/kJ²], [$/kJ2], [USD/kJ2], [usd/kJ2]
[£/kJ²] | British Pounds per Kilo Joule Square | [GBP/kJ²], [gbp/kJ²], [£/kJ2], [GBP/kJ2], [gbp/kJ2]
[€/kJ²] | Euro per Kilo Joule Square | [EUR/kJ²], [eur/kJ²], [€/kJ2], [EUR/kJ2], [eur/kJ2]
[$/J²] | US Dollar per Watt Hour Square | [USD/J²], [usd/J²], [$/J2], [USD/J2], [usd/J2]
[£/J²] | British Pounds per Joule Square | [GBP/J²], [gbp/J²], [£/J2], [GBP/J2], [gbp/J2]
[€/J²] | Euro per Joule Square | [EUR/J²], [eur/J²], [€/J2], [EUR/J2], [eur/J2]
[$/MMBTU²] | US Dollar per Millions of British Thermal Unit Square | [USD/MMBTU²], [usd/MMBTU²], [$/MMbtu²], [USD/MMbtu²], [usd/MMbtu²], [$/mmbtu²], [USD/mmbtu²], [usd/mmbtu²], [$/MMBTU2], [USD/MMBTU2], [usd/MMBTU2], [$/MMbtu2], [USD/MMbtu2], [usd/MMbtu2], [$/mmbtu2], [USD/mmbtu2], [usd/mmbtu2]
[£/MMBTU²] | British Pounds per Millions of British Thermal Unit Square | [GBP/MMBTU²], [gbp/MMBTU²], [£/MMbtu²], [GBP/MMbtu²], [gbp/MMbtu²], [£/mmbtu²], [GBP/mmbtu²], [gbp/mmbtu²], [£/MMBTU2], [GBP/MMBTU2], [gbp/MMBTU2], [£/MMbtu2], [GBP/MMbtu2], [gbp/MMbtu2], [£/mmbtu2], [GBP/mmbtu2], [gbp/mmbtu2]
[€/MMBTU²] | Euro per Millions of British Thermal Unit Square | [EUR/MMBTU²], [eur/MMBTU²], [€/MMbtu²], [EUR/MMbtu²], [eur/MMbtu²], [€/mmbtu²], [EUR/mmbtu²], [eur/mmbtu²], [€/MMBTU2], [EUR/MMBTU2], [eur/MMBTU2], [€/MMbtu2], [EUR/MMbtu2], [eur/MMbtu2], [€/mmbtu2], [EUR/mmbtu2], [eur/mmbtu2]
[$/MBTU²] | US Dollar per Thousands of British Thermal Unit Square | [USD/MBTU²], [usd/MBTU²], [$/Mbtu²], [USD/Mbtu²], [usd/Mbtu²], [$/mbtu²], [USD/mbtu²], [usd/mbtu²], [$/MBTU2], [USD/MBTU2], [usd/MBTU2], [$/Mbtu2], [USD/Mbtu2], [usd/Mbtu2], [$/mbtu2], [USD/mbtu2], [usd/mbtu2]
[£/MBTU²] | British Pounds per Thousands of British Thermal Unit Square | [GBP/MBTU²], [gbp/MBTU²], [£/Mbtu²], [GBP/Mbtu²], [gbp/Mbtu²], [£/mbtu²], [GBP/mbtu²], [gbp/mbtu²], [£/MBTU2], [GBP/MBTU2], [gbp/MBTU2], [£/Mbtu2], [GBP/Mbtu2], [gbp/Mbtu2], [£/mbtu2], [GBP/mbtu2], [gbp/mbtu2]
[€/MBTU²] | Euro per Thousands of British Thermal Unit Square | [EUR/MBTU²], [eur/MBTU²], [€/Mbtu²], [EUR/Mbtu²], [eur/Mbtu²], [€/mbtu²], [EUR/mbtu²], [eur/mbtu²], [€/MBTU2], [EUR/MBTU2], [eur/MBTU2], [€/Mbtu2], [EUR/Mbtu2], [eur/Mbtu2], [€/mbtu2], [EUR/mbtu2], [eur/mbtu2]
[$/BTU²] | US Dollar per British Thermal Unit Square | [USD/BTU²], [usd/BTU²], [$/Btu²], [USD/Btu²], [usd/Btu²], [$/btu²], [USD/btu²], [usd/btu²], [$/BTU2], [USD/BTU2], [usd/BTU2], [$/Btu2], [USD/Btu2], [usd/Btu2], [$/btu2], [USD/btu2], [usd/btu2]
[£/BTU²] | British Pounds per British Thermal Unit Square | [GBP/BTU²], [gbp/BTU²], [£/Btu²], [GBP/Btu²], [gbp/Btu²], [£/btu²], [GBP/btu²], [gbp/btu²], [£/BTU2], [GBP/BTU2], [gbp/BTU2], [£/Btu2], [GBP/Btu2], [gbp/Btu2], [£/btu2], [GBP/btu2], [gbp/btu2]
[€/BTU²] | Euro per British Thermal Unit Square | [EUR/BTU²], [eur/BTU²], [€/Btu²], [EUR/Btu²], [eur/Btu²], [€/btu²], [EUR/btu²], [eur/btu²], [€/BTU2], [EUR/BTU2], [eur/BTU2], [€/Btu2], [EUR/Btu2], [eur/Btu2], [€/btu2], [EUR/btu2], [eur/btu2]
VOLPRC | Price per Volume
[$/m³] | US Dollar per Cubic Meter | [USD/m³], [usd/m³], [$/m3], [USD/m3], [usd/m3]
[£/m³] | British Pounds per Cubic Meter | [GBP/m³], [gbp/m³], [£/m3], [GBP/m3], [gbp/m3]
[€/m³] | Euro per Cubic Meter | [EUR/m³], [eur/m³], [€/m3], [EUR/m3], [eur/m3]
[$/ft³] | US Dollar per Cubic Feet | [USD/ft³], [usd/ft³], [$/ft3], [USD/ft3], [usd/ft3]
[£/ft³] | British Pounds per Cubic Feet | [GBP/ft³], [gbp/ft³], [£/ft3], [GBP/ft3], [gbp/ft3]
[€/ft³] | Euro per Cubic Feet | [EUR/ft³], [eur/ft³], [€/ft3], [EUR/ft3], [eur/ft3]

## ENET
Name | BaseF [Hz] = 50 | BaseS [MVA] = 100 | CRSType = NONE | Info
ENET39 | 60 | 100 | DEFAULT | -

## ESUB
Name | Info
IEEE39 | -

## EGRP
Name | Info
NUCLEAR | NUCLEAR GENERATORS
COAL | COAL GENERATORS
GAS | GAS GENERATORS
WIND | WIND GENERATORS
PV | PV GENERATORS

## EZN
Name | Info
IEEE39 | -

## ENO
Name | Alias | BaseV [kV] = 20 | H [m] = 0 | Info | InService = True | Visible = True | VMAXDEF [pu] = 1.1 | VMINDEF [pu] = 0.9 | X/Long [-] = 0 | Y/Lat [-] = 0 | ZoneName = ZONE1
ALBANY_NY | Bus 1 | 345 | 0 | - | TRUE | TRUE | 1.1 | 0.9 | -73.7401 | 42.6616 | IEEE39
GREENFIELD_MA | Bus 2 | 345 | 0 | - | TRUE | TRUE | 1.1 | 0.9 | -72.5789 | 42.5872 | IEEE39
HOLYOKE_MA | Bus 3 | 345 | 0 | - | TRUE | TRUE | 1.1 | 0.9 | -72.5892 | 42.1988 | IEEE39
HARTFORD_CT | Bus 4 | 345 | 0 | - | TRUE | TRUE | 1.1 | 0.9 | -72.7844 | 41.7631 | IEEE39
PROSPECT_CT | Bus 5 | 345 | 0 | - | TRUE | TRUE | 1.1 | 0.9 | -72.9758 | 41.5042 | IEEE39
NEWHAVEN_CT | Bus 6 | 345 | 0 | - | TRUE | TRUE | 1.1 | 0.9 | -72.9082 | 41.3108 | IEEE39
ANSONIA_CT | Bus 7 | 345 | 0 | - | TRUE | TRUE | 1.1 | 0.9 | -73.0857 | 41.348 | IEEE39
SOUTHBURY_CT | Bus 8 | 345 | 0 | - | TRUE | TRUE | 1.1 | 0.9 | -73.1234 | 41.4848 | IEEE39
DANBURY_CT | Bus 9 | 345 | 0 | - | TRUE | TRUE | 1.1 | 0.9 | -73.4022 | 41.3914 | IEEE39
GROTON_CT | Bus 10 | 345 | 0 | - | TRUE | TRUE | 1.1 | 0.9 | -72.0464 | 41.3733 | IEEE39
NEWLONDON_CT | Bus 11 | 345 | 0 | - | TRUE | TRUE | 1.1 | 0.9 | -72.105 | 41.3657 | IEEE39
NEWLONDON2_CT | Bus 12 | 25 | 0 | - | TRUE | TRUE | 1.1 | 0.9 | -72.104 | 41.3681 | IEEE39
GROTON2_CT | Bus 13 | 345 | 0 | - | TRUE | TRUE | 1.1 | 0.9 | -72.0856 | 41.3734 | IEEE39
MARLBOROUGH_CT | Bus 14 | 345 | 0 | - | TRUE | TRUE | 1.1 | 0.9 | -72.4445 | 41.7008 | IEEE39
PROVIDENCE_RI | Bus 15 | 345 | 0 | - | TRUE | TRUE | 1.1 | 0.9 | -71.4053 | 41.8162 | IEEE39
BOSTON_MA | Bus 16 | 345 | 0 | - | TRUE | TRUE | 1.1 | 0.9 | -71.1686 | 42.2803 | IEEE39
WORCESTER_MA | Bus 17 | 345 | 0 | - | TRUE | TRUE | 1.1 | 0.9 | -71.7357 | 42.2743 | IEEE39
BRIMFIELD_MA | Bus 18 | 345 | 0 | - | TRUE | TRUE | 1.1 | 0.9 | -72.2093 | 42.1584 | IEEE39
FALLRIVER_MA | Bus 19 | 345 | 0 | - | TRUE | TRUE | 1.1 | 0.9 | -71.1851 | 41.7611 | IEEE39
FALLRIVER2_MA | Bus 20 | 345 | 0 | - | TRUE | TRUE | 1.1 | 0.9 | -71.1675 | 41.7554 | IEEE39
BROCKTON_MA | Bus 21 | 345 | 0 | - | TRUE | TRUE | 1.1 | 0.9 | -71.0044 | 42.0754 | IEEE39
MIDDLEBOROUGH_MA | Bus 22 | 345 | 0 | - | TRUE | TRUE | 1.1 | 0.9 | -70.9038 | 41.8914 | IEEE39
HYANNIS_MA | Bus 23 | 345 | 0 | - | TRUE | TRUE | 1.1 | 0.9 | -70.285 | 41.6862 | IEEE39
QUINCY_MA | Bus 24 | 345 | 0 | - | TRUE | TRUE | 1.1 | 0.9 | -70.9922 | 42.2543 | IEEE39
BRATTLEBORO_VT | Bus 25 | 345 | 0 | - | TRUE | TRUE | 1.1 | 0.9 | -72.5191 | 42.7829 | IEEE39
NASHUA_NH | Bus 26 | 345 | 0 | - | TRUE | TRUE | 1.1 | 0.9 | -71.4544 | 42.765 | IEEE39
LITTLETON_MA | Bus 27 | 345 | 0 | - | TRUE | TRUE | 1.1 | 0.9 | -71.5302 | 42.5686 | IEEE39
PORTLAND_ME | Bus 28 | 345 | 0 | - | TRUE | TRUE | 1.1 | 0.9 | -70.2924 | 43.6544 | IEEE39
AUGUSTA_ME | Bus 29 | 345 | 0 | - | TRUE | TRUE | 1.1 | 0.9 | -69.8035 | 44.2543 | IEEE39
TURNERSFALLS_MA | Bus 30 | 20 | 0 | - | TRUE | TRUE | 1.1 | 0.9 | -72.5769 | 42.5884 | IEEE39
NEWHAVEN2_CT | Bus 31 | 20 | 0 | - | TRUE | TRUE | 1.1 | 0.9 | -72.9088 | 41.3073 | IEEE39
MYSTIC_CT | Bus 32 | 20 | 0 | - | TRUE | TRUE | 1.1 | 0.9 | -72.0422 | 41.3727 | IEEE39
FALLRIVER4_MA | Bus 33 | 20 | 0 | - | TRUE | TRUE | 1.1 | 0.9 | -71.185 | 41.7323 | IEEE39
FALLRIVER3_MA | Bus 34 | 20 | 0 | - | TRUE | TRUE | 1.1 | 0.9 | -71.1463 | 41.8018 | IEEE39
MIDDLEBOROUGH2_MA | Bus 35 | 20 | 0 | - | TRUE | TRUE | 1.1 | 0.9 | -70.9049 | 41.8906 | IEEE39
HYANNIS2_MA | Bus 36 | 20 | 0 | - | TRUE | TRUE | 1.1 | 0.9 | -70.2837 | 41.6818 | IEEE39
BRATTLEBORO2_VT | Bus 37 | 20 | 0 | - | TRUE | TRUE | 1.1 | 0.9 | -72.5159 | 42.78 | IEEE39
AUGUSTA2_ME | Bus 38 | 20 | 0 | - | TRUE | TRUE | 1.1 | 0.9 | -69.8035 | 44.2551 | IEEE39
KINGSTON_NY | Bus 39 | 345 | 0 | - | TRUE | TRUE | 1.1 | 0.9 | -74.0215 | 41.911 | IEEE39

## LI
Name | FromName | ToName | Alias | BB0DEF [pu] = 0 | BB0L [μS/km] = 0 | BBDEF [pu] = 0 | BBL [μS/km] = 0 | CalcImp = False | DrawLine = False | IMAXDEF [A] = ∞ | Info | InService = True | L [km] = 10 | N [-] = 1 | PHASESINUSE = ABC | PMAXDEF [MW] = ∞ | PMAXPRCDEF [$/MWh] = ∞ | PMAXREVDEF [MW] = ∞ | PMAXREVPRCDEF [$/MWh] = ∞ | RATEDS [MVA] = NaN | RATEDV [kV] = NaN | RR0DEF [pu] = 0 | RR0L [Ω/km] = 0 | RRDEF [pu] = 0 | RRL [Ω/km] = 0 | SMAXDEF [MVA] = ∞ | SubName | Visible = True | XX0DEF [pu] = 0 | XX0L [Ω/km] = 0 | XXDEF [pu] = 0 | XXL [Ω/km] = 0
ALBANY_NY_TO_GREENFIELD_MA | ALBANY_NY | GREENFIELD_MA | - | 0.2329 | 0 | 0.6987 | 0 | FALSE | FALSE | 1200 | - | TRUE | 95.44 | 1 | ABC | 700 | ∞ | 700 | ∞ | NaN | NaN | 0.0105 | 0 | 0.0035 | 0 | 750 | IEEE39 | TRUE | 0.1233 | 0 | 0.0411 | 0
ALBANY_NY_TO_KINGSTON_NY | ALBANY_NY | KINGSTON_NY | - | 0.25 | 0 | 0.75 | 0 | FALSE | FALSE | 1200 | - | TRUE | 86.69 | 1 | ABC | 700 | ∞ | 700 | ∞ | NaN | NaN | 0.003 | 0 | 0.001 | 0 | 750 | IEEE39 | TRUE | 0.075 | 0 | 0.025 | 0
DANBURY_CT_TO_KINGSTON_NY | DANBURY_CT | KINGSTON_NY | - | 0.4 | 0 | 1.2 | 0 | FALSE | FALSE | 1200 | - | TRUE | 77.42 | 1 | ABC | 700 | ∞ | 700 | ∞ | NaN | NaN | 0.003 | 0 | 0.001 | 0 | 750 | IEEE39 | TRUE | 0.075 | 0 | 0.025 | 0
GREENFIELD_MA_TO_HOLYOKE_MA | GREENFIELD_MA | HOLYOKE_MA | - | 0.085733 | 0 | 0.2572 | 0 | FALSE | FALSE | 1200 | - | TRUE | 43.24 | 1 | ABC | 700 | ∞ | 700 | ∞ | NaN | NaN | 0.0039 | 0 | 0.0013 | 0 | 750 | IEEE39 | TRUE | 0.0453 | 0 | 0.0151 | 0
GREENFIELD_MA_TO_BRATTLEBORO_VT | GREENFIELD_MA | BRATTLEBORO_VT | - | 0.048667 | 0 | 0.146 | 0 | FALSE | FALSE | 1200 | - | TRUE | 21.91 | 1 | ABC | 700 | ∞ | 700 | ∞ | NaN | NaN | 0.021 | 0 | 0.007 | 0 | 750 | IEEE39 | TRUE | 0.0258 | 0 | 0.0086 | 0
HOLYOKE_MA_TO_HARTFORD_CT | HOLYOKE_MA | HARTFORD_CT | - | 0.0738 | 0 | 0.2214 | 0 | FALSE | FALSE | 1200 | - | TRUE | 51.1 | 1 | ABC | 700 | ∞ | 700 | ∞ | NaN | NaN | 0.0039 | 0 | 0.0013 | 0 | 750 | IEEE39 | TRUE | 0.0639 | 0 | 0.0213 | 0
HOLYOKE_MA_TO_BRIMFIELD_MA | HOLYOKE_MA | BRIMFIELD_MA | - | 0.071267 | 0 | 0.2138 | 0 | FALSE | FALSE | 1200 | - | TRUE | 31.66 | 1 | ABC | 700 | ∞ | 700 | ∞ | NaN | NaN | 0.0033 | 0 | 0.0011 | 0 | 750 | IEEE39 | TRUE | 0.0399 | 0 | 0.0133 | 0
WORCESTER_MA_TO_BRIMFIELD_MA | WORCESTER_MA | BRIMFIELD_MA | - | 0.043967 | 0 | 0.1319 | 0 | FALSE | FALSE | 1200 | - | TRUE | 41.1 | 1 | ABC | 700 | ∞ | 700 | ∞ | NaN | NaN | 0.0021 | 0 | 0.0007 | 0 | 750 | IEEE39 | TRUE | 0.0246 | 0 | 0.0082 | 0
HARTFORD_CT_TO_PROSPECT_CT | HARTFORD_CT | PROSPECT_CT | - | 0.044733 | 0 | 0.1342 | 0 | FALSE | FALSE | 1200 | - | TRUE | 32.92 | 1 | ABC | 700 | ∞ | 700 | ∞ | NaN | NaN | 0.0024 | 0 | 0.0008 | 0 | 750 | IEEE39 | TRUE | 0.0384 | 0 | 0.0128 | 0
HARTFORD_CT_TO_MARLBOROUGH_CT | HARTFORD_CT | MARLBOROUGH_CT | - | 0.046067 | 0 | 0.1382 | 0 | FALSE | FALSE | 1200 | - | TRUE | 29.07 | 1 | ABC | 700 | ∞ | 700 | ∞ | NaN | NaN | 0.0024 | 0 | 0.0008 | 0 | 750 | IEEE39 | TRUE | 0.0387 | 0 | 0.0129 | 0
GROTON2_CT_TO_MARLBOROUGH_CT | GROTON2_CT | MARLBOROUGH_CT | - | 0.057433 | 0 | 0.1723 | 0 | FALSE | FALSE | 1200 | - | TRUE | 47.13 | 1 | ABC | 700 | ∞ | 700 | ∞ | NaN | NaN | 0.0027 | 0 | 0.0009 | 0 | 750 | IEEE39 | TRUE | 0.0303 | 0 | 0.0101 | 0
PROSPECT_CT_TO_NEWHAVEN_CT | PROSPECT_CT | NEWHAVEN_CT | - | 0.014467 | 0 | 0.0434 | 0 | FALSE | FALSE | 1200 | - | TRUE | 22.25 | 1 | ABC | 700 | ∞ | 700 | ∞ | NaN | NaN | 0.0006 | 0 | 0.0002 | 0 | 750 | IEEE39 | TRUE | 0.0078 | 0 | 0.0026 | 0
PROSPECT_CT_TO_SOUTHBURY_CT | PROSPECT_CT | SOUTHBURY_CT | - | 0.0492 | 0 | 0.1476 | 0 | FALSE | FALSE | 1200 | - | TRUE | 12.49 | 1 | ABC | 700 | ∞ | 700 | ∞ | NaN | NaN | 0.0024 | 0 | 0.0008 | 0 | 750 | IEEE39 | TRUE | 0.0336 | 0 | 0.0112 | 0
ANSONIA_CT_TO_SOUTHBURY_CT | ANSONIA_CT | SOUTHBURY_CT | - | 0.026 | 0 | 0.078 | 0 | FALSE | FALSE | 1200 | - | TRUE | 15.54 | 1 | ABC | 700 | ∞ | 700 | ∞ | NaN | NaN | 0.0012 | 0 | 0.0004 | 0 | 750 | IEEE39 | TRUE | 0.0138 | 0 | 0.0046 | 0
NEWHAVEN_CT_TO_ANSONIA_CT | NEWHAVEN_CT | ANSONIA_CT | - | 0.037667 | 0 | 0.113 | 0 | FALSE | FALSE | 1200 | - | TRUE | 15.4 | 1 | ABC | 700 | ∞ | 700 | ∞ | NaN | NaN | 0.0018 | 0 | 0.0006 | 0 | 750 | IEEE39 | TRUE | 0.0276 | 0 | 0.0092 | 0
NEWHAVEN_CT_TO_NEWLONDON_CT | NEWHAVEN_CT | NEWLONDON_CT | - | 0.0463 | 0 | 0.1389 | 0 | FALSE | FALSE | 1200 | - | TRUE | 67.39 | 1 | ABC | 700 | ∞ | 700 | ∞ | NaN | NaN | 0.0021 | 0 | 0.0007 | 0 | 750 | IEEE39 | TRUE | 0.0246 | 0 | 0.0082 | 0
GROTON_CT_TO_NEWLONDON_CT | GROTON_CT | NEWLONDON_CT | - | 0.0243 | 0 | 0.0729 | 0 | FALSE | FALSE | 1200 | - | TRUE | 4.97 | 1 | ABC | 700 | ∞ | 700 | ∞ | NaN | NaN | 0.0012 | 0 | 0.0004 | 0 | 750 | IEEE39 | TRUE | 0.0129 | 0 | 0.0043 | 0
SOUTHBURY_CT_TO_DANBURY_CT | SOUTHBURY_CT | DANBURY_CT | - | 0.1268 | 0 | 0.3804 | 0 | FALSE | FALSE | 1200 | - | TRUE | 25.46 | 1 | ABC | 700 | ∞ | 700 | ∞ | NaN | NaN | 0.0069 | 0 | 0.0023 | 0 | 750 | IEEE39 | TRUE | 0.1089 | 0 | 0.0363 | 0
GROTON_CT_TO_GROTON2_CT | GROTON_CT | GROTON2_CT | - | 0.0243 | 0 | 0.0729 | 0 | FALSE | FALSE | 1200 | - | TRUE | 3.28 | 1 | ABC | 700 | ∞ | 700 | ∞ | NaN | NaN | 0.0012 | 0 | 0.0004 | 0 | 750 | IEEE39 | TRUE | 0.0129 | 0 | 0.0043 | 0
MARLBOROUGH_CT_TO_PROVIDENCE_RI | MARLBOROUGH_CT | PROVIDENCE_RI | - | 0.122 | 0 | 0.366 | 0 | FALSE | FALSE | 1200 | - | TRUE | 87.22 | 1 | ABC | 700 | ∞ | 700 | ∞ | NaN | NaN | 0.0054 | 0 | 0.0018 | 0 | 750 | IEEE39 | TRUE | 0.0651 | 0 | 0.0217 | 0
PROVIDENCE_RI_TO_BOSTON_MA | PROVIDENCE_RI | BOSTON_MA | - | 0.057 | 0 | 0.171 | 0 | FALSE | FALSE | 1200 | - | TRUE | 55.22 | 1 | ABC | 700 | ∞ | 700 | ∞ | NaN | NaN | 0.0027 | 0 | 0.0009 | 0 | 750 | IEEE39 | TRUE | 0.0282 | 0 | 0.0094 | 0
BOSTON_MA_TO_WORCESTER_MA | BOSTON_MA | WORCESTER_MA | - | 0.044733 | 0 | 0.1342 | 0 | FALSE | FALSE | 1200 | - | TRUE | 46.7 | 1 | ABC | 700 | ∞ | 700 | ∞ | NaN | NaN | 0.0021 | 0 | 0.0007 | 0 | 750 | IEEE39 | TRUE | 0.0267 | 0 | 0.0089 | 0
BOSTON_MA_TO_FALLRIVER_MA | BOSTON_MA | FALLRIVER_MA | - | 0.10133 | 0 | 0.304 | 0 | FALSE | FALSE | 1200 | - | TRUE | 57.8 | 1 | ABC | 700 | ∞ | 700 | ∞ | NaN | NaN | 0.0048 | 0 | 0.0016 | 0 | 750 | IEEE39 | TRUE | 0.0585 | 0 | 0.0195 | 0
BOSTON_MA_TO_BROCKTON_MA | BOSTON_MA | BROCKTON_MA | - | 0.084933 | 0 | 0.2548 | 0 | FALSE | FALSE | 1200 | - | TRUE | 26.52 | 1 | ABC | 700 | ∞ | 700 | ∞ | NaN | NaN | 0.0024 | 0 | 0.0008 | 0 | 750 | IEEE39 | TRUE | 0.0405 | 0 | 0.0135 | 0
BOSTON_MA_TO_QUINCY_MA | BOSTON_MA | QUINCY_MA | - | 0.022667 | 0 | 0.068 | 0 | FALSE | FALSE | 1200 | - | TRUE | 14.82 | 1 | ABC | 700 | ∞ | 700 | ∞ | NaN | NaN | 0.0009 | 0 | 0.0003 | 0 | 750 | IEEE39 | TRUE | 0.0177 | 0 | 0.0059 | 0
HYANNIS_MA_TO_QUINCY_MA | HYANNIS_MA | QUINCY_MA | - | 0.12033 | 0 | 0.361 | 0 | FALSE | FALSE | 1200 | - | TRUE | 86.14 | 1 | ABC | 700 | ∞ | 700 | ∞ | NaN | NaN | 0.0066 | 0 | 0.0022 | 0 | 750 | IEEE39 | TRUE | 0.105 | 0 | 0.035 | 0
WORCESTER_MA_TO_LITTLETON_MA | WORCESTER_MA | LITTLETON_MA | - | 0.1072 | 0 | 0.3216 | 0 | FALSE | FALSE | 1200 | - | TRUE | 36.85 | 1 | ABC | 700 | ∞ | 700 | ∞ | NaN | NaN | 0.0039 | 0 | 0.0013 | 0 | 750 | IEEE39 | TRUE | 0.0519 | 0 | 0.0173 | 0
NASHUA_NH_TO_LITTLETON_MA | NASHUA_NH | LITTLETON_MA | - | 0.079867 | 0 | 0.2396 | 0 | FALSE | FALSE | 1200 | - | TRUE | 22.72 | 1 | ABC | 700 | ∞ | 700 | ∞ | NaN | NaN | 0.0042 | 0 | 0.0014 | 0 | 750 | IEEE39 | TRUE | 0.0441 | 0 | 0.0147 | 0
BROCKTON_MA_TO_MIDDLEBOROUGH_MA | BROCKTON_MA | MIDDLEBOROUGH_MA | - | 0.0855 | 0 | 0.2565 | 0 | FALSE | FALSE | 1200 | - | TRUE | 22.1 | 1 | ABC | 700 | ∞ | 700 | ∞ | NaN | NaN | 0.0024 | 0 | 0.0008 | 0 | 750 | IEEE39 | TRUE | 0.042 | 0 | 0.014 | 0
MIDDLEBOROUGH_MA_TO_HYANNIS_MA | MIDDLEBOROUGH_MA | HYANNIS_MA | - | 0.061533 | 0 | 0.1846 | 0 | FALSE | FALSE | 1200 | - | TRUE | 56.19 | 1 | ABC | 700 | ∞ | 700 | ∞ | NaN | NaN | 0.0018 | 0 | 0.0006 | 0 | 750 | IEEE39 | TRUE | 0.0288 | 0 | 0.0096 | 0
BRATTLEBORO_VT_TO_NASHUA_NH | BRATTLEBORO_VT | NASHUA_NH | - | 0.171 | 0 | 0.513 | 0 | FALSE | FALSE | 1200 | - | TRUE | 86.65 | 1 | ABC | 700 | ∞ | 700 | ∞ | NaN | NaN | 0.0096 | 0 | 0.0032 | 0 | 750 | IEEE39 | TRUE | 0.0969 | 0 | 0.0323 | 0
NASHUA_NH_TO_PORTLAND_ME | NASHUA_NH | PORTLAND_ME | - | 0.26007 | 0 | 0.7802 | 0 | FALSE | FALSE | 1200 | - | TRUE | 136.67 | 1 | ABC | 700 | ∞ | 700 | ∞ | NaN | NaN | 0.0129 | 0 | 0.0043 | 0 | 750 | IEEE39 | TRUE | 0.1422 | 0 | 0.0474 | 0
NASHUA_NH_TO_AUGUSTA_ME | NASHUA_NH | AUGUSTA_ME | - | 0.343 | 0 | 1.029 | 0 | FALSE | FALSE | 1200 | - | TRUE | 212.66 | 1 | ABC | 700 | ∞ | 700 | ∞ | NaN | NaN | 0.0171 | 0 | 0.0057 | 0 | 750 | IEEE39 | TRUE | 0.1875 | 0 | 0.0625 | 0
PORTLAND_ME_TO_AUGUSTA_ME | PORTLAND_ME | AUGUSTA_ME | - | 0.083 | 0 | 0.249 | 0 | FALSE | FALSE | 1200 | - | TRUE | 77.41 | 1 | ABC | 700 | ∞ | 700 | ∞ | NaN | NaN | 0.0042 | 0 | 0.0014 | 0 | 750 | IEEE39 | TRUE | 0.0453 | 0 | 0.0151 | 0

## TRF
Name | FromName | ToName | Alias | BBDEF [pu] = 0 | CalcImp = False | CTRLMODE = TapSet | D [pu] = 0 | DrawLine = False | FROMRATEDV [kV] = 200 | GGDEF [pu] = 0 | IMAXDEF [A] = ∞ | Info | InService = True | IOL [%] = 0 | N [-] = 1 | PCU [MW] = 0.1 | PFE [MW] = 0 | PHASESINUSE = ABC | PHISETDEF [deg] = 0 | PMAXDEF [MW] = ∞ | PMAXPRCDEF [$/MWh] = ∞ | PMAXREVDEF [MW] = ∞ | PMAXREVPRCDEF [$/MWh] = ∞ | QSETDEF [pu] = 1 | RATEDS [MVA] = NaN | RDROP [pu] = 0 | RemoteName | RRDEF [pu] = 0 | SMAXDEF [MVA] = ∞ | SubName | TAPMAX [-] = 2 | TAPMIN [-] = -2 | TAPN [-] = 0 | TAPSETDEF [-] = 0 | TAPSide = From | TAPSTEP [%] = 5 | TORATEDV [kV] = 200 | TRFModel = PI | Visible = True | VMSETDEF [pu] = 1 | VSC [%] = 0.1 | XDROP [pu] = 0 | XXDEF [pu] = 0
GREENFIELD_MA_TO_TURNERSFALLS_MA | GREENFIELD_MA | TURNERSFALLS_MA | - | 0 | FALSE | TapSet | 0 | FALSE | 353.625 | 0 | ∞ | - | TRUE | 0 | 1 | 0.1 | 0 | ABC | 0 | 1000 | ∞ | 1000 | ∞ | 1 | NaN | 0 | - | 0.00181 | 1200 | IEEE39 | 16 | -16 | 0 | 0 | From | 0.625 | 20 | PI | TRUE | 1 | 0.1 | 0 | 0.0181
NEWHAVEN_CT_TO_NEWHAVEN2_CT | NEWHAVEN_CT | NEWHAVEN2_CT | - | 0 | FALSE | Voltage | 0 | FALSE | 345 | 0 | ∞ | - | TRUE | 0 | 1 | 0.1 | 0 | ABC | 0 | 1000 | ∞ | 1000 | ∞ | 1 | NaN | 0 | NEWHAVEN_CT | 0.0025 | 1200 | IEEE39 | 16 | -16 | 0 | 0 | From | 0.625 | 19.86 | PI | TRUE | 1.01 | 0.1 | 0 | 0.025
GROTON_CT_TO_MYSTIC_CT | GROTON_CT | MYSTIC_CT | - | 0 | FALSE | TapSet | 0 | FALSE | 369.15 | 0 | ∞ | - | TRUE | 0 | 1 | 0.1 | 0 | ABC | 0 | 1000 | ∞ | 1000 | ∞ | 1 | NaN | 0 | - | 0.002 | 1200 | IEEE39 | 16 | -16 | 0 | 0 | From | 0.625 | 20 | PI | TRUE | 1 | 0.1 | 0 | 0.02
NEWLONDON_CT_TO_NEWLONDON2_CT | NEWLONDON_CT | NEWLONDON2_CT | - | 0 | FALSE | TapSet | 0 | FALSE | 345 | 0 | ∞ | - | TRUE | 0 | 1 | 0.1 | 0 | ABC | 0 | 1000 | ∞ | 1000 | ∞ | 1 | NaN | 0 | - | 0.0016 | 1200 | IEEE39 | 16 | -16 | 0 | 0 | From | 0.625 | 25.15 | PI | TRUE | 1 | 0.1 | 0 | 0.0435
GROTON2_CT_TO_NEWLONDON2_CT | GROTON2_CT | NEWLONDON2_CT | - | 0 | FALSE | TapSet | 0 | FALSE | 345 | 0 | ∞ | - | TRUE | 0 | 1 | 0.1 | 0 | ABC | 0 | 1000 | ∞ | 1000 | ∞ | 1 | NaN | 0 | - | 0.0016 | 1200 | IEEE39 | 16 | -16 | 0 | 0 | From | 0.625 | 25.15 | PI | TRUE | 1 | 0.1 | 0 | 0.0435
FALLRIVER_MA_TO_FALLRIVER2_MA | FALLRIVER_MA | FALLRIVER2_MA | - | 0 | FALSE | TapSet | 0 | FALSE | 365.7 | 0 | ∞ | - | TRUE | 0 | 1 | 0.1 | 0 | ABC | 0 | 1000 | ∞ | 1000 | ∞ | 1 | NaN | 0 | - | 0.0007 | 1200 | IEEE39 | 16 | -16 | 0 | 0 | From | 0.625 | 345 | PI | TRUE | 1 | 0.1 | 0 | 0.0138
FALLRIVER_MA_TO_FALLRIVER4_MA | FALLRIVER_MA | FALLRIVER4_MA | - | 0 | FALSE | TapSet | 0 | FALSE | 369.15 | 0 | ∞ | - | TRUE | 0 | 1 | 0.1 | 0 | ABC | 0 | 1000 | ∞ | 1000 | ∞ | 1 | NaN | 0 | - | 0.0007 | 1200 | IEEE39 | 16 | -16 | 0 | 0 | From | 0.625 | 20 | PI | TRUE | 1 | 0.1 | 0 | 0.0142
FALLRIVER2_MA_TO_FALLRIVER3_MA | FALLRIVER2_MA | FALLRIVER3_MA | - | 0 | FALSE | TapSet | 0 | FALSE | 348.105 | 0 | ∞ | - | TRUE | 0 | 1 | 0.1 | 0 | ABC | 0 | 1000 | ∞ | 1000 | ∞ | 1 | NaN | 0 | - | 0.0009 | 1200 | IEEE39 | 16 | -16 | 0 | 0 | From | 0.625 | 20 | PI | TRUE | 1 | 0.1 | 0 | 0.018
MIDDLEBOROUGH_MA_TO_MIDDLEBOROUGH2_MA | MIDDLEBOROUGH_MA | MIDDLEBOROUGH2_MA | - | 0 | FALSE | TapSet | 0 | FALSE | 353.625 | 0 | ∞ | - | TRUE | 0 | 1 | 0.1 | 0 | ABC | 0 | 1000 | ∞ | 1000 | ∞ | 1 | NaN | 0 | - | 0.0004 | 1200 | IEEE39 | 16 | -16 | 0 | 0 | From | 0.625 | 20 | PI | TRUE | 1 | 0.1 | 0 | 0.0143
HYANNIS_MA_TO_HYANNIS2_MA | HYANNIS_MA | HYANNIS2_MA | - | 0 | FALSE | TapSet | 0 | FALSE | 345 | 0 | ∞ | - | TRUE | 0 | 1 | 0.1 | 0 | ABC | 0 | 1000 | ∞ | 1000 | ∞ | 1 | NaN | 0 | - | 0.0005 | 1200 | IEEE39 | 16 | -16 | 0 | 0 | From | 0.625 | 20 | PI | TRUE | 1 | 0.1 | 0 | 0.0272
BRATTLEBORO_VT_TO_BRATTLEBORO2_VT | BRATTLEBORO_VT | BRATTLEBORO2_VT | - | 0 | FALSE | TapSet | 0 | FALSE | 353.625 | 0 | ∞ | - | TRUE | 0 | 1 | 0.1 | 0 | ABC | 0 | 1000 | ∞ | 1000 | ∞ | 1 | NaN | 0 | - | 0.0006 | 1200 | IEEE39 | 16 | -16 | 0 | 0 | From | 0.625 | 20 | PI | TRUE | 1 | 0.1 | 0 | 0.0232
AUGUSTA_ME_TO_AUGUSTA2_ME | AUGUSTA_ME | AUGUSTA2_ME | - | 0 | FALSE | TapSet | 0 | FALSE | 353.625 | 0 | ∞ | - | TRUE | 0 | 1 | 0.1 | 0 | ABC | 0 | 1000 | ∞ | 1000 | ∞ | 1 | NaN | 0 | - | 0.0008 | 1200 | IEEE39 | 16 | -16 | 0 | 0 | From | 0.625 | 20 | PI | TRUE | 1 | 0.1 | 0 | 0.0156

## EDEM
Name | NodeName | Alias | Info | InService = True | LOADTYPE = Wye | PMAXDEF [MW] = ∞ | PMAXPRCDEF [$/MWh] = ∞ | PMINDEF [MW] = 0 | PMINPRCDEF [$/MWh] = ∞ | PSETDEF [MW] = 0 | PSETPRCDEF [$/MWh] = 2000 | PWF [-] = 1 | PWFType = ind | QMAXDEF [MVAr] = ∞ | QMINDEF [MVAr] = -∞ | RATEDV [kV] = NaN | Visible = True
HOLYOKE_DEMAND | HOLYOKE_MA | - | - | TRUE | Wye | ∞ | ∞ | 0 | ∞ | 322 | 100000 | 0.99997 | ind | ∞ | -∞ | 345 | TRUE
HARTFORD_DEMAND | HARTFORD_CT | - | - | TRUE | Wye | ∞ | ∞ | 0 | ∞ | 500 | 100000 | 0.93847 | ind | ∞ | -∞ | 345 | TRUE
ANSONIA_DEMAND | ANSONIA_CT | - | - | TRUE | Wye | ∞ | ∞ | 0 | ∞ | 233.8 | 100000 | 0.9411 | ind | ∞ | -∞ | 345 | TRUE
SOUTHBURY_DEMAND | SOUTHBURY_CT | - | - | TRUE | Wye | ∞ | ∞ | 0 | ∞ | 522 | 100000 | 0.94759 | ind | ∞ | -∞ | 345 | TRUE
NEWLONDON2_DEMAND | NEWLONDON2_CT | - | - | TRUE | Wye | ∞ | ∞ | 0 | ∞ | 7.5 | 100000 | 0.08492 | ind | ∞ | -∞ | 25 | TRUE
PROVIDENCE_DEMAND | PROVIDENCE_RI | - | - | TRUE | Wye | ∞ | ∞ | 0 | ∞ | 320 | 100000 | 0.90218 | ind | ∞ | -∞ | 345 | TRUE
BOSTON_DEMAND | BOSTON_MA | - | - | TRUE | Wye | ∞ | ∞ | 0 | ∞ | 329.4 | 100000 | 0.99523 | ind | ∞ | -∞ | 345 | TRUE
BRIMFIELD_DEMAND | BRIMFIELD_MA | - | - | TRUE | Wye | ∞ | ∞ | 0 | ∞ | 158 | 100000 | 0.98245 | ind | ∞ | -∞ | 345 | TRUE
FALLRIVER2_DEMAND | FALLRIVER2_MA | - | - | TRUE | Wye | ∞ | ∞ | 0 | ∞ | 628 | 100000 | 0.98682 | ind | ∞ | -∞ | 345 | TRUE
BROCKTON_DEMAND | BROCKTON_MA | - | - | TRUE | Wye | ∞ | ∞ | 0 | ∞ | 274 | 100000 | 0.92208 | ind | ∞ | -∞ | 345 | TRUE
HYANNIS_DEMAND | HYANNIS_MA | - | - | TRUE | Wye | ∞ | ∞ | 0 | ∞ | 274.5 | 100000 | 0.95564 | ind | ∞ | -∞ | 345 | TRUE
QUINCY_DEMAND | QUINCY_MA | - | - | TRUE | Wye | ∞ | ∞ | 0 | ∞ | 308.6 | 100000 | 0.95815 | cap | ∞ | -∞ | 345 | TRUE
BRATTLEBORO_DEMAND | BRATTLEBORO_VT | - | - | TRUE | Wye | ∞ | ∞ | 0 | ∞ | 224 | 100000 | 0.97851 | ind | ∞ | -∞ | 345 | TRUE
NASHUA_DEMAND | NASHUA_NH | - | - | TRUE | Wye | ∞ | ∞ | 0 | ∞ | 139 | 100000 | 0.9926 | ind | ∞ | -∞ | 345 | TRUE
LITTLETON_DEMAND | LITTLETON_MA | - | - | TRUE | Wye | ∞ | ∞ | 0 | ∞ | 281 | 100000 | 0.96575 | ind | ∞ | -∞ | 345 | TRUE
PORTLAND_DEMAND | PORTLAND_ME | - | - | TRUE | Wye | ∞ | ∞ | 0 | ∞ | 206 | 100000 | 0.99114 | ind | ∞ | -∞ | 345 | TRUE
AUGUSTA_DEMAND | AUGUSTA_ME | - | - | TRUE | Wye | ∞ | ∞ | 0 | ∞ | 283.5 | 100000 | 0.99553 | ind | ∞ | -∞ | 345 | TRUE
NEWHAVEN2_DEMAND | NEWHAVEN2_CT | - | - | TRUE | Wye | ∞ | ∞ | 0 | ∞ | 9.2 | 100000 | 0.89443 | ind | ∞ | -∞ | 20 | TRUE
KINGSTON_DEMAND | KINGSTON_NY | - | - | TRUE | Wye | ∞ | ∞ | 0 | ∞ | 1104 | 100000 | 0.97531 | ind | ∞ | -∞ | 345 | TRUE

## ESTR
Name | NodeName | Alias | GENPHASES = ABC | Info | InService = True | MaxCapDef [MJ] = ∞ | MaxDownRampDef [MW/min] = ∞ | MaxUpRampDef [MW/min] = ∞ | MinDownTimeDDDef [h] = 0 | MinDownTimeDGDef [h] = 0 | MinDownTimeGDDef [h] = 0 | MinDownTimeGGDef [h] = 0 | MinUpTimeDDef [h] = 0 | MinUpTimeGDef [h] = 0 | PDeff [-] = 1 | PDMAXDEF [MW] = ∞ | PDMAXPRCDEF [$/MWh] = ∞ | PDMINDEF [MW] = 0 | PDMINPRCDEF [$/MWh] = ∞ | PFSETDEF [-] = 0 | PGeff [-] = 1 | PGMAXDEF [MW] = ∞ | PGMAXPRCDEF [$/MWh] = ∞ | PGMINDEF [MW] = 0 | PGMINPRCDEF [$/MWh] = ∞ | PSETDEF [MW] = 0 | PSETPRCDEF [$/MWh] = 2000 | QMAXDEF [MVAr] = ∞ | QMINDEF [MVAr] = -∞ | QSETDEF [MVAr] = 0 | SOCMAXPRCDEF [$/MWh] = 1000000 | SOCMINPRCDEF [$/MWh] = 1000000 | SOCSETPRCDEF [$/MWh] = 1000000 | Visible = True | VOMDPriceDef [$/MWh] = 0 | VOMGPriceDef [$/MWh] = 0
HARTFORD_CT_STORAGE | HARTFORD_CT | - | ABC | - | TRUE | 18419294.6387 | ∞ | ∞ | 0 | 0 | 0 | 0 | 0 | 0 | 0.96 | 98 | ∞ | 0 | ∞ | 0 | 0.96 | 98 | ∞ | 0 | ∞ | 0 | 2000 | ∞ | -∞ | 0 | 1000000 | 1000000 | 1000000 | TRUE | 0 | 0
SOUTHBURY_CT_STORAGE | SOUTHBURY_CT | - | ABC | - | TRUE | 169312395.6272 | ∞ | ∞ | 0 | 0 | 0 | 0 | 0 | 0 | 0.96 | 2467 | ∞ | 0 | ∞ | 0 | 0.96 | 2467 | ∞ | 0 | ∞ | 0 | 2000 | ∞ | -∞ | 0 | 1000000 | 1000000 | 1000000 | TRUE | 0 | 0
WORCESTER_MA_STORAGE | WORCESTER_MA | - | ABC | - | TRUE | 1749119.3401 | ∞ | ∞ | 0 | 0 | 0 | 0 | 0 | 0 | 0.96 | 42 | ∞ | 0 | ∞ | 0 | 0.96 | 42 | ∞ | 0 | ∞ | 0 | 2000 | ∞ | -∞ | 0 | 1000000 | 1000000 | 1000000 | TRUE | 0 | 0
QUINCY_MA_STORAGE | QUINCY_MA | - | ABC | - | TRUE | 53788013.5243 | ∞ | ∞ | 0 | 0 | 0 | 0 | 0 | 0 | 0.96 | 1202 | ∞ | 0 | ∞ | 0 | 0.96 | 1202 | ∞ | 0 | ∞ | 0 | 2000 | ∞ | -∞ | 0 | 1000000 | 1000000 | 1000000 | TRUE | 0 | 0
LITTLETON_MA_STORAGE | LITTLETON_MA | - | ABC | - | TRUE | 68775888.8016 | ∞ | ∞ | 0 | 0 | 0 | 0 | 0 | 0 | 0.96 | 1668 | ∞ | 0 | ∞ | 0 | 0.96 | 1668 | ∞ | 0 | ∞ | 0 | 2000 | ∞ | -∞ | 0 | 1000000 | 1000000 | 1000000 | TRUE | 0 | 0
AUGUSTA2_ME_STORAGE | AUGUSTA2_ME | - | ABC | - | TRUE | 11283460.5385 | ∞ | ∞ | 0 | 0 | 0 | 0 | 0 | 0 | 0.96 | 148 | ∞ | 0 | ∞ | 0 | 0.96 | 148 | ∞ | 0 | ∞ | 0 | 2000 | ∞ | -∞ | 0 | 1000000 | 1000000 | 1000000 | TRUE | 0 | 0
KINGSTON_NY_STORAGE | KINGSTON_NY | - | ABC | - | TRUE | 2777167.2109 | ∞ | ∞ | 0 | 0 | 0 | 0 | 0 | 0 | 0.96 | 93 | ∞ | 0 | ∞ | 0 | 0.96 | 93 | ∞ | 0 | ∞ | 0 | 2000 | ∞ | -∞ | 0 | 1000000 | 1000000 | 1000000 | TRUE | 0 | 0

## SHT
Name | NodeName | Alias | BSETDEF [MVAr] = 0 | GSETDEF [MW] = 0 | Info | InService = True | RATEDV [kV] = NaN | SHTTYPE = Wye | Visible = True
SHUNT_0 | HARTFORD_CT | - | 100 | 0 | - | TRUE | 345 | Wye | TRUE
SHUNT_1 | PROSPECT_CT | - | 200 | 0 | - | TRUE | 345 | Wye | TRUE

## WIND
Name | NodeName | Alias | C0DEF [$] = 0 | C1DEF [$/MWh] = 0 | C2DEF [$/MWh2] = 0 | CALCDFLT = SELECT | HubHeight [m] = 100 | Info | InService = True | Lat [-] = 0 | Long [-] = 0 | LOSSES [%] = 14.08 | MaxDownRampDef [MW/min] = ∞ | MaxUpRampDef [MW/min] = ∞ | PFSETDEF [-] = 0 | PMAXDEF [MW] = ∞ | PMAXPRCDEF [$/MWh] = ∞ | PMINDEF [MW] = 0 | PMINPRCDEF [$/MWh] = ∞ | PSETDEF [MW] = 0 | PSETPRCDEF [$/MWh] = 2000 | QMAXDEF [MVAr] = ∞ | QMINDEF [MVAr] = -∞ | QSETDEF [MVAr] = 0 | RATEDS [MVA] = NaN | RATEDV [kV] = NaN | RRN [pu] = 0 | RRSE [pu] = 0 | Visible = True | VOMPriceDef [$/MWh] = 0 | WDFile | WTPCName | XXN [pu] = 0 | XXSE [pu] = 0
FAIRHAVEN | FALLRIVER_MA | - | 0 | 0 | 0 | SELECT | 100 | - | TRUE | 41.7175 | -71.1186 | 14.08 | ∞ | ∞ | 0 | 0 | ∞ | 0 | ∞ | 0 | 0 | 40 | -40 | 0 | 200 | 345 | 0 | 0.001 | TRUE | 0 | - | - | 0 | 0.001
CAMELOT | MIDDLEBOROUGH_MA | - | 0 | 0 | 0 | SELECT | 100 | - | TRUE | 41.6688 | -71.0836 | 14.08 | ∞ | ∞ | 0 | 64 | ∞ | 0 | ∞ | 0 | 0 | 30 | -30 | 0 | 150 | 345 | 0 | 0.001 | TRUE | 0 | - | - | 0 | 0.001
BEAVERRIDGE | AUGUSTA_ME | - | 0 | 0 | 0 | SELECT | 100 | - | TRUE | 44.0442 | -69.7632 | 14.08 | ∞ | ∞ | 0 | 0 | ∞ | 0 | ∞ | 0 | 0 | 20 | -20 | 0 | 100 | 345 | 0 | 0.001 | TRUE | 0 | - | - | 0 | 0.001

## PV
Name | NodeName | Alias | ArrayType = Fixed | Azimuth [deg] = 180 | C0DEF [$] = 0 | C1DEF [$/MWh] = 0 | C2DEF [$/MWh2] = 0 | CALCDFLT = SELECT | DCACRatio [-] = 1.1 | GENPHASES = ABC | IMAXPU [pu] = 1.1 | Info | InService = True | InvEff [%] = 96 | Lat [-] = 0 | Long [-] = 0 | LOSSES [%] = 14.08 | MaxDownRampDef [MW/min] = ∞ | MaxUpRampDef [MW/min] = ∞ | ModuleType = Standard | PFSETDEF [-] = 0 | PMAXDEF [MW] = ∞ | PMAXPRCDEF [$/MWh] = ∞ | PMINDEF [MW] = 0 | PMINPRCDEF [$/MWh] = ∞ | PSETDEF [MW] = 0 | PSETPRCDEF [$/MWh] = 2000 | QMAXDEF [MVAr] = ∞ | QMINDEF [MVAr] = -∞ | QSETDEF [MVAr] = 0 | RATEDS [MVA] = NaN | RATEDV [kV] = NaN | Tilt [deg] = 0 | Visible = True | VMAXPU [pu] = 1.1 | VMINPU [pu] = 0.9 | VOMPriceDef [$/MWh] = 0 | WDFile
QUINEBAUG | HARTFORD_CT | - | Fixed | 180 | 0 | 0 | 0 | SELECT | 1.1 | ABC | 1.1 | - | TRUE | 96 | 41.7631 | -72.7844 | 14.08 | ∞ | ∞ | Standard | 0 | 1330 | ∞ | 0 | ∞ | 0 | 0 | 30 | -30 | 0 | 150 | 345 | 35 | TRUE | 1.1 | 0.9 | 0 | WeatherData\Solar_ad4505ee460147bc8e869230fe60b076_41.76312_-72.78442_2021_60.P3Sr.csv
WALLINGFORD | SOUTHBURY_CT | - | Fixed | 180 | 0 | 0 | 0 | SELECT | 1.1 | ABC | 1.1 | - | TRUE | 96 | 41.4798 | -73.1909 | 14.08 | ∞ | ∞ | Standard | 0 | 5451 | ∞ | 0 | ∞ | 0 | 0 | 40 | -40 | 0 | 200 | 345 | 35 | TRUE | 1.1 | 0.9 | 0 | WeatherData\Solar_2b2bc61028964557870e8f9cd92cc5d3_41.47978_-73.19092_2021_60.P3Sr.csv
RAVENBROOK | FALLRIVER2_MA | - | Fixed | 180 | 0 | 0 | 0 | SELECT | 1.1 | ABC | 1.1 | - | TRUE | 96 | 41.6975 | -71.142 | 14.08 | ∞ | ∞ | Standard | 0 | 0 | ∞ | 0 | ∞ | 0 | 0 | 30 | -30 | 0 | 150 | 345 | 35 | TRUE | 1.1 | 0.9 | 0 | WeatherData\Solar_a2069d4a8c67454394c42c4db24ab6c0_41.69753_-71.14197_2021_60.P3Sr.csv
CANTON | QUINCY_MA | - | Fixed | 180 | 0 | 0 | 0 | SELECT | 1.1 | ABC | 1.1 | - | TRUE | 96 | 42.255 | -70.9882 | 14.08 | ∞ | ∞ | Standard | 0 | 2972 | ∞ | 0 | ∞ | 0 | 0 | 20 | -20 | 0 | 100 | 345 | 35 | TRUE | 1.1 | 0.9 | 0 | WeatherData\Solar_a30c0835544f41bf92e1a0dade6d81da_42.25495_-70.98816_2021_60.P3Sr.csv
SHAFFER | LITTLETON_MA | - | Fixed | 180 | 0 | 0 | 0 | SELECT | 1.1 | ABC | 1.1 | - | TRUE | 96 | 42.5126 | -71.5347 | 14.08 | ∞ | ∞ | Standard | 0 | 3953 | ∞ | 0 | ∞ | 0 | 0 | 10 | -10 | 0 | 50 | 345 | 35 | TRUE | 1.1 | 0.9 | 0 | WeatherData\Solar_b1ec062780e04f15b9089ffb2c7a9340_42.5126_-71.53473_2021_60.P3Sr.csv
WINSLOW | AUGUSTA_ME | - | Fixed | 180 | 0 | 0 | 0 | SELECT | 1.1 | ABC | 1.1 | - | TRUE | 96 | 44.0955 | -69.8511 | 14.08 | ∞ | ∞ | Standard | 0 | 662 | ∞ | 0 | ∞ | 0 | 0 | 10 | -10 | 0 | 50 | 345 | 35 | TRUE | 1.1 | 0.9 | 0 | WeatherData\Solar_d0b3e295c8b74c5fa3ecbf1957b375fd_44.09548_-69.85107_2021_60.P3Sr.csv

## FUEL
Name | Alias | CO2 [g/FuelUnit] = 0 | FuelPriceDef [€/FuelUnit] = 0 | FuelUnit = [m³] | Info | InService = True | NOX [g/FuelUnit] = 0 | SO2 [g/FuelUnit] = 0
URANIUM | - | 0 | 0.8 | [MMBTU] | - | TRUE | 0 | 0
NATURAL_GAS | - | 53454 | 4.5 | [MMBTU] | - | TRUE | 36.24 | 0.272
COAL | - | 95130 | 2.75 | [MMBTU] | - | TRUE | 36.29 | 40.82

## FGEN
Name | FuelName | NodeName | Alias | C0DEF [$] = 0 | C1DEF [$/MWh] = 0 | C2DEF [$/MWh2] = 0 | CALCDFLT = SELECT | EFFMAX [-] = 0.7 | EFFMIN [-] = 0.24 | FC0 [FuelUnit/h] = 0 | FC1 [FuelUnit/h/MW] = 0 | FC2 [FuelUnit/h/MW²] = 0 | GenType = GASTURBINE | HR0 [MJ/kWh] = 0 | HR1 [MJ/kWh/MW] = 0 | HR2 [MJ/kWh/MW2] = 0 | Info | InService = True | MaxDownRampDef [MW/min] = ∞ | MaxUpRampDef [MW/min] = ∞ | MinDownTimeDef [h] = 0 | MinUpTimeDef [h] = 0 | NSEG [-] = 2 | PFSETDEF [-] = 0 | PMAXDEF [MW] = ∞ | PMAXPRCDEF [$/MWh] = ∞ | PMINDEF [MW] = 0 | PMINPRCDEF [$/MWh] = ∞ | PSETDEF [MW] = 0 | PSETPRCDEF [$/MWh] = 2000 | QMAXDEF [MVAr] = ∞ | QMINDEF [MVAr] = -∞ | RATEDS [MVA] = NaN | RATEDV [kV] = NaN | RRN [pu] = 0 | RRSE [pu] = 0 | ShutDownPriceDef [$] = 0 | StartUpPriceDef [$] = 0 | Visible = True | VMSETDEF [pu] = 1 | VOMPriceDef [$/MWh] = 0 | XXN [pu] = 0 | XXSE [pu] = 0
SIMONDS | NATURAL_GAS | TURNERSFALLS_MA | - | 0 | 7 | 0 | SELECT | 0.7 | 0.24 | 175 | 10.5 | 0 | CCGT | 12.91 | -0.00622 | 0 | - | TRUE | 0.20833 | 0.20833 | 4 | 4 | 2 | 0 | 0 | ∞ | 112.5 | ∞ | 250 | 2000 | 170 | -140 | 300 | NaN | 0 | 0 | 0 | 11700 | TRUE | 1.048 | 7 | 0 | 0
BRIDGEPORT | COAL | NEWHAVEN2_CT | - | 0 | 10 | 0 | SELECT | 0.7 | 0.24 | 737 | 10.26 | 0 | COAL | 12.82 | -0.0018 | 0 | - | TRUE | 2 | 2 | 24 | 24 | 2 | 1 | 0 | ∞ | 400 | ∞ | 547.326 | 2000 | 660 | -530 | 1200 | NaN | 0 | 0 | 0 | 59000 | TRUE | 0.982 | 10 | 0 | 0
MILLSTONE | URANIUM | MYSTIC_CT | - | 0 | 5 | 0 | SELECT | 0.7 | 0.24 | 6400 | 0.05 | 0 | NUCLEAR | 18.254 | -0.014 | 0 | - | TRUE | 1 | 1 | 168 | 168 | 2 | 0 | 0 | ∞ | 645 | ∞ | 650 | 2000 | 430 | -340 | 780 | NaN | 0 | 0 | 0 | 104000 | TRUE | 0.983 | 5 | 0 | 0
DARTMOUTH | NATURAL_GAS | FALLRIVER4_MA | - | 0 | 7 | 0 | SELECT | 0.7 | 0.24 | 100 | 8 | 0 | CCGT | 8.545 | -0.00056 | 0 | - | TRUE | 3.16 | 3.16 | 4 | 4 | 2 | 0 | 0 | ∞ | 284.4 | ∞ | 632 | 2000 | 400 | -320 | 750 | NaN | 0 | 0 | 0 | 29600 | TRUE | 0.997 | 7 | 0 | 0
DIGHTON | NATURAL_GAS | FALLRIVER3_MA | - | 0 | 7 | 0 | SELECT | 0.7 | 0.24 | 45 | 7.5 | 0 | CCGT | 7.805 | -0.00039 | 0 | - | TRUE | 2.54 | 2.54 | 4 | 4 | 2 | 0 | 0 | ∞ | 228.6 | ∞ | 508 | 2000 | 320 | -260 | 600 | NaN | 0 | 0 | 0 | 23700 | TRUE | 1.012 | 7 | 0 | 0
FORERIVER | NATURAL_GAS | MIDDLEBOROUGH2_MA | - | 0 | 7 | 0 | SELECT | 0.7 | 0.24 | 125 | 9.5 | 0 | CCGT | 10.162 | -0.00066 | 0 | - | TRUE | 3.25 | 3.25 | 4 | 4 | 2 | 0 | 0 | ∞ | 292.5 | ∞ | 650 | 2000 | 430 | -340 | 780 | NaN | 0 | 0 | 0 | 30400 | TRUE | 1.049 | 7 | 0 | 0
CLEARLYFLOOD | NATURAL_GAS | HYANNIS2_MA | - | 0 | 7 | 0 | SELECT | 0.7 | 0.24 | 250 | 7 | 0 | CCGT | 8.538 | -0.00177 | 0 | - | TRUE | 2.8 | 2.8 | 4 | 4 | 2 | 0 | 0 | ∞ | 252 | ∞ | 560 | 2000 | 390 | -310 | 680 | NaN | 0 | 0 | 0 | 26200 | TRUE | 1.064 | 7 | 0 | 0
VERMONT_YANKEE | URANIUM | BRATTLEBORO2_VT | - | 0 | 5 | 0 | SELECT | 0.7 | 0.24 | 5400 | 0.15 | 0 | NUCLEAR | 18.4 | -0.0167 | 0 | - | TRUE | 1 | 1 | 168 | 168 | 2 | 0 | 0 | ∞ | 535 | ∞ | 540 | 2000 | 360 | -290 | 650 | NaN | 0 | 0 | 0 | 86400 | TRUE | 1.028 | 5 | 0 | 0
WESTBROOK | NATURAL_GAS | AUGUSTA2_ME | - | 0 | 7 | 0 | SELECT | 0.7 | 0.24 | 500 | 8.5 | 0 | CCGT | 10.575 | -0.00161 | 0 | - | TRUE | 4.15 | 4.15 | 4 | 4 | 2 | 0 | 0 | ∞ | 373.5 | ∞ | 830 | 2000 | 560 | -450 | 1000 | NaN | 0 | 0 | 0 | 38800 | TRUE | 1.027 | 7 | 0 | 0
DANSKAMMER | COAL | KINGSTON_NY | - | 0 | 10 | 0 | SELECT | 0.7 | 0.24 | 771 | 10.15 | 0 | COAL | 12.85 | -0.0019 | 0 | - | TRUE | 2 | 2 | 24 | 24 | 2 | 0 | 0 | ∞ | 400 | ∞ | 1000 | 2000 | 660 | -530 | 1200 | NaN | 0 | 0 | 0 | 61000 | TRUE | 1.03 | 10 | 0 | 0

## ASVC
Name | Alias | ASVCType = UpReserve | Unit = [MW] | Info | InService = True | MinValDef = 0 | MinValPriceDef = 0
RESERVE_REQUIREMENT | - | UpReserve | [MW] | SYSTEM WIDE 10-MINUTE UPWARD RAMPING REQUIREMENT | TRUE | 0 | 10000

## ASVCX
Name | Alias | ASVCPriceDef = 0 | Info | InService = True | MaxValDef = 0 | ASVCName | External
SIMONDS_RESERVE_CONTRIBUTION | - | 0 | - | TRUE | 0 | RESERVE_REQUIREMENT | FGEN.SIMONDS
DARTMOUTH_RESERVE_CONTRIBUTION | - | 0 | - | TRUE | 0 | RESERVE_REQUIREMENT | FGEN.DARTMOUTH
DIGHTON_RESERVE_CONTRIBUTION | - | 0 | - | TRUE | 0 | RESERVE_REQUIREMENT | FGEN.DIGHTON
FORERIVER_RESERVE_CONTRIBUTION | - | 0 | - | TRUE | 0 | RESERVE_REQUIREMENT | FGEN.FORERIVER
CLEARLYFLOOD_RESERVE_CONTRIBUTION | - | 0 | - | TRUE | 0 | RESERVE_REQUIREMENT | FGEN.CLEARLYFLOOD
WESTBROOK_RESERVE_CONTRIBUTION | - | 0 | - | TRUE | 0 | RESERVE_REQUIREMENT | FGEN.WESTBROOK
BRIDGEPORT_RESERVE_CONTRIBUTION | - | 0 | - | TRUE | 0 | RESERVE_REQUIREMENT | FGEN.BRIDGEPORT
DANSKAMMER_RESERVE_CONTRIBUTION | - | 0 | - | TRUE | 0 | RESERVE_REQUIREMENT | FGEN.DANSKAMMER

## ECNSTR
Name | Alias | AvgLowBoundDef [-] = -∞ | AvgUpBoundDef [-] = ∞ | Info | InService = True | LowBoundDef [-] = -∞ | UpBoundDef [-] = ∞
ECNSTR_0 | - | 0 | 100 | - | TRUE | 0 | 100
ECNSTR_1 | - | 0 | 100 | - | TRUE | 0 | 100
ECNSTR_2 | - | 10 | 90 | - | TRUE | 10 | 90
ECNSTR_3 | - | 10 | 90 | - | TRUE | 10 | 90
ECNSTR_4 | - | 10 | 90 | - | TRUE | 10 | 90

## EVAR
Name | Alias | CoeffDef [-] = 1 | Info | InService = False | ObjVarName = NONE | Unit | CNSTRName | NetObjID
EVAR_0 | - | 1 | - | TRUE | PG | [MW] | ECNSTR_0 | ESTR.ESTR_0
EVAR_1 | - | 1 | - | TRUE | PD | [MW] | ECNSTR_1 | ESTR.ESTR_0
EVAR_2 | - | 1 | - | TRUE | SOC | [%] | ECNSTR_2 | ESTR.ESTR_0
EVAR_3 | - | 1 | - | TRUE | SOC | [%] | ECNSTR_3 | ESTR.ESTR_0
EVAR_4 | - | 1 | - | TRUE | SOC | [%] | ECNSTR_4 | ESTR.ESTR_0

## EGRPM
[GRPM] | NUCLEAR
FGEN.MILLSTONE
FGEN.VERMONT_YANKEE
[GRPM] | COAL
FGEN.BRIDGEPORT
FGEN.DANSKAMMER
[GRPM] | GAS
FGEN.CLEARLYFLOOD
FGEN.DARTMOUTH
FGEN.DIGHTON
FGEN.FORERIVER
FGEN.SIMONDS
FGEN.WESTBROOK
[GRPM] | WIND
WIND.BEAVERRIDGE
WIND.CAMELOT
WIND.FAIRHAVEN
[GRPM] | PV
PV.CANTON
PV.QUINEBAUG
PV.RAVENBROOK
PV.SHAFFER
PV.WALLINGFORD
PV.WINSLOW